SAVE WATER PROJECT

SUPPLY AND DELIVERY OF EQUIPMENT FOR THE WATER SUPPLY SYSTEM

VLORE, ALBANIA

Content of dossier

 CONTRACT NOTICE

 ADDITIONAL INFORMATION ABOUT THE CONTRACT NOTICE

 LETTER OF INVITATION

 INSTRUCTIONS TO TENDERERS

 DRAFT CONTRACT

 SPECIAL CONDITIONS

 GENERAL CONDITIONS

 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER (Lot 1&Lot 2)

 BUDGET BREAKDOWN

 ADMINISTRATIVE COMPLIANCE GRID

 EVALUATION GRID

 TENDER FORM FOR A SUPPLY CONTRACT

 DECLARATION ON HONOUR ON EXCLUSION AND SELECTION CRITERIA

 PROVISIONAL / FINAL ACCEPTANCE CERTIFICATE (Lot 1&Lot 2)

 FINANCIAL IDENTIFICATION

 LEGAL ENTITY – NATURAL PERSON

 LEGAL ENTITY - PRIVATE/PUBLIC LAW BODY WITH LEGAL FORM

 LEGAL ENTITY – PUBLIC LAW BODY

 External action financial instruments and European Development Fund. Rules on participation in procurement procedures and grants

CONTRACT NOTICE

CALL FOR TENDER: GENERAL INFORMATION

- I.1) Name and address Contracting Authority

Official name: Regional Council of Vlore
Postal address: Pallati i Kultures “Laberia”, kati III
Town: Vlore
Postal Code: 9401
E-mail: info@qarkuvlore.gov.al
Internet address: www.qarkuvlore.gov.al

II.1.1) Title: Water Supply Products for the Water Supply System (supply and installation) / LOT 1 and Sensors for the monitoring of Water Supply System (supply and installation) / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

- II.1.2) Main CPV code 42000000-6   

II.1.3) Type of contract

Supplies

- II.1.4) Short description of the contract

The pilot action of the project is based on two main actions:

- The intervention in the water supply system for the improvement of the existing one for saving the drinking water of the water supply in the administrative units of Vlore municipality which correspondents with the Lot 1 of the relevant Tender. Submersible electric pumps, Centrifugal electric pumps, Vertical Centrifugal Electric Pumps and other equipment are necessary to be delivered and installed at the relevant sites of Water Supply in Vlora municipality, in total 11 sites. Centrifugal type water pumps can be installed at the request of the project to ensure proper pressure and flow throughout the day in a building. Pumps must be equipped with water meter, pressure gauge, relevant pipes connecting the pump to the water supply system, their respective electrical panel, relay protection system, thermal protection, as well as the automatic control system of work.

- ICT upgrades of monitoring infrastructure correspondents with the Lot 2 of the relevant Tender. Besides the supply with the relevant equipment it is foreseen to focus the monitoring of water flow in terms of quantity and quality at a pilot site which will be in Babice e Madhe village, part of Qender- Shushice administrative unit. The monitoring will be realized with the monitoring system through sensors that will be installed and will be monitored by using the Water Management and Monitoring Data Center and other tools available for facilitating the process. It should be considered that the sensors will be installed at an outdoor site.

- II.1.5) Estimated total value

- Currency:  LEK

- IV.1.1.) Type of Procedure

- Open

- N/A

- [In case of previous publication of prior information notice: IV.2.1) Previous publication concerning this procedure

- Notice number in the OJ S:  <4 digits number >/S <2 to 3 digits number>-<5 digits number>

- II.1.6) Information about lots

- This contract is divided into lots: Yes

- In case of lots Tenders may be submitted for:
all lots
maximum number of lots:  2


CALL FOR TENDER: INFORMATION PER LOT

II.2) Description

II.2.1)
Lot no.: 1
Title: Water Supply Products for the Water Supply System (supply and installation) for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

- [In case of lots, each lot must have at least one CPV code. See heading II.1.2 for information on CPV codes.

- II.2.2) Additional CPV code(s)

- Main CPV code 42122000-0

Lot no.: 2
Title: Sensors for the monitoring of Water Supply System (supply and installation) for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

[In case of lots, each lot must have at least one CPV code. See heading II.1.2 for information on CPV codes.

- II.2.2) Additional CPV code(s)

- Main CPV code 30230000-0

- II.2.3) Place of performance

- Geographical zone benefitting from the action: Municipality of Vlore

- II.2.5) Award Criteria

- Price

- II.2.6 Estimated value

- Currency:  LEK

- N/A

- II.2.14) Additional information

- Provided they are in conformity with the basic project, new services or works consisting in the repetition of similar services or works, may be entrusted up to [percentage] of the initial contract to the initial contractor by negotiated procedure without prior publication of a contract notice.

- IV.2.2) Time limit for submission of tenders or requests to participate

- Date: 15/09/2022
Local Time [in case of publication through PPMT: (Central European Time): 16:00

- IV.2.6) Minimum time frame during which the tenderer must maintain the tender

- Duration in months:  three months (from the date stated for receipt of tender)

- IV.2.7) Conditions for opening of tenders

- Date: 19/09/2022
Local time [in case of publication through PPMT: (Central European Time)]: 10:00
Place: Vlore, Regional Council of Vlore premises

Additional information about the Contract Notice

Water Supply Products for the Water Supply System (supply and installation) / LOT 1 and Sensors for the monitoring of Water Supply System (supply and installation) / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

Vlore, Albania

Nature of contract

For supply contracts: lump sum

Programme title

Interreg Cross Border Programme Greece Albania 2014-2020

Financing

Project Subsidy Contract A1-1.1-2

Legal basis, eligibility and rules of origin

For IPA III 2021/1529:

The legal basis of this procedure is <Regulation (EU) No [2021/1529] establishing the Instrument for Pre-accession Assistance (IPA III)>. See Annex A2 of the practical guide.

For this contract award procedure, participation is open to all natural persons who are nationals of and legal persons (participating either individually or in a grouping – consortium – of candidates/tenderers) which are effectively established in a Member State of the European Union or in an eligible country or territory as defined under Article 10 of Regulation (EU) No [2021/1529] establishing the Instrument for Pre-accession Assistance (IPA III).

For supply contracts: All supplies under this contract may originate in any country.

Added Note for the programme 2014-2020 (under IPA II):

General budget of the Union for calls where the CIR does not apply (e.g. for IPA I):  Participation is open to all legal persons (participating either individually or in a grouping – consortium – of tenderers) which are established in a Member State of the European Union or in a country or territory of the regions covered and/or authorised by the specific instruments applicable to the programme under which the contract is financed (see item ‘Legal basis’  below). Participation is also open to international organisations. Participation of natural persons is directly governed by the specific instruments applicable to the programme under which the contract is financed].

For works and supply contracts All supplies under this contract must originate in one or more of these countries.

Candidature

All eligible natural and legal persons (as per item 4 above) or groupings of such persons (consortia) may participate or tender.

A consortium may be a permanent, legally established grouping or a grouping which has been constituted informally for a specific procurement procedure. All partners of a consortium (i.e., the leader and all other partners) are jointly and severally liable to the contracting authority.

The participation or tender of an ineligible natural or legal person will result in the automatic exclusion of that person. In particular, if that ineligible person belongs to a consortium, the whole consortium will be excluded.

Number of requests to participate or tenders

No more than one request to participate or tender can be submitted by a natural or legal person whatever the form of participation (as an individual legal entity or as leader or partner of a consortium submitting a request to participate or tender). In the event that a natural or legal person submits more than one request to participate or tender, all requests to participate or tenders in which that person has participated will be excluded.

In case of lots, the candidates or tenderers may submit only one request to participate or tender per lot. Contracts will be awarded lot by lot and each lot will form a separate contract.

Grounds for exclusion

Candidates must submit a signed declaration, included in the request to participate form, to the effect that they are not in any of the situations listed in Section 2.6.10.1 of the practical guide (PRAG). Where the candidate intends to rely on capacity providing entities or subcontractor(s), he/she must provide the same declaration signed by this/these entity(ies).

Candidates included in the lists of EU restrictive measures (see Section 2.4. of the PRAG) at the moment of the award decision cannot be awarded the contract.

Sub-contracting

Sub-contracting is allowed.

Number of candidates to be short-listed

On the basis of the request to participate received, between 4 and [for service contracts: 8] [for works contracts: 6] candidates will be invited to submit detailed tenders for this contract. If the number of eligible candidates meeting the selection criteria is less than the minimum of 4, the contracting authority may invite the candidates who satisfy the criteria to submit a tender. If the number of eligible candidates meeting the selection criteria is more than the maximum allowed, the contracting authority will rank them using the re-examination criteria stated below.

Short-list alliances prohibited

Any tenders received from tenderers having a different composition that the ones mentioned in the short-listed request to participate forms will be excluded from this restricted tender procedure, unless prior approval from the contracting authority has been obtained – see practical guide 2.6.3. Short-listed candidates may not form alliances or subcontract to each other for the contract in question.

Provisional date of invitation to tender

12.08.2022

Provisional commencement date of the contract

30.09.2022

Period of implementation of tasks

30.09.2022-30.12.2022

Language of the procedure

All written communications for this tender procedure and contract must be in English.

Additional information

Financial data to be provided by the candidate in the request to participate form or in the tender submission form must be expressed in LEK.

only for indirect management in the following cases: (i) when legal or local constraints exceptionally impose using the national currency; (ii) when needed, for contracts within the imprest component of a programme estimate]. If applicable, where a candidate refers to amounts originally expressed in a different currency, the conversion to LEK only for indirect management in the following cases: (i) when legal or local constraints exceptionally impose using the national currency; (ii) when needed, for contracts within the imprest component of a programme estimate] shall be made in accordance with the InforEuro exchange rate of MONTH and YEAR of the applicable InforEuro exchange rate, which can either correspond to the month and year of the publication of the present contract notice or the month and year corresponding to the deadline for submitting requests to participate, which can be found at the following address: http://ec.europa.eu/budget/graphs/inforeuro.html.

SELECTION CRITERIA

Selection criteria

Capacity-providing entities

An economic operator (i.e. candidate or tenderer) may, where appropriate and for a particular contract, rely on the capacities of other entities, regardless of the legal nature of the links which it has with them. If the economic operator relies on other entities, it must in that case prove to the contracting authority that it will have at its disposal the resources necessary for the performance of the contract by producing a commitment by those entities to place those resources at its disposal. Such entities, for instance the parent company of the economic operator, must respect the same rules of eligibility and notably that of nationality as the economic operator relying on them and must comply with the selection criteria for which the economic operator relies on them. Furthermore, the data for this third entity for the relevant selection criterion should be included in a separate document. Proof of the capacity will also have to be provided when requested by the contracting authority.

With regard to technical and professional criteria, an economic operator may only rely on the capacities of other entities where the latter will perform the tasks for which these capacities are required.

With regard to economic and financial criteria, the entities upon whose capacity the economic operator relies, become jointly and severally liable for the performance of the contract.

The following selection criteria will be applied to candidates. In the case of requests to participate submitted by a consortium, these selection criteria will be applied to the consortium as a whole if not specified otherwise. The selection criteria will not be applied to natural persons and single-member companies when they are sub-contractors.

The candidate shall not use previous experience which caused breach of contract and termination by a contracting authority as a reference for selection criteria.

- Lot n° 1:

The selection criteria for tenderers to lot n° 1 are as follows:

Economic and financial capacity of candidate

- will not be economically dependent on the contracting authority in the event that the contract is awarded to it

- has sufficient financial stability to handle the proposed contract.>

- the average annual turnover of the tenderer must exceed the annualised maximum budget of the contract i.e. the maximum budget stated in the contract notice divided by the initial contract duration in years, where this exceeds 1 year (minimum annual turnover requested may not exceed 2 times the estimated annual contract value, except in duly justified cases motivated in the tender dossier);

- Current ratio (current assets/current liabilities) in the last year for which accounts have been closed must be at least 1. In case of a consortium this criterion must be fulfilled by each member.

- the available financial resources of the tenderer must exceed the annualised maximum budget of the contract i.e. the maximum budget stated in the contract notice divided by the initial contract duration in years, where this exceeds 1 year (minimum annual turnover requested may not exceed 2 times the estimated annual contract value, except in duly justified cases motivated in the tender dossier); and

- the financial situation of the tenderer should not be in deficit, considered debts, at the beginning and end of year.

Professional capacity of candidate

- A technical group composed by at least: 3 specialists of the relevant fields: Construction engineer, mechanical engineer, electrical engineer

- at least 1 professional certificate appropriate to this contract such as delivery and installation of water supply pumps

- at least 1 professional certificate appropriate to this contract such as construction for the installation of the water supplies

Technical capacity of candidate

- the tenderer has delivered supplies under at least 1 contract with a budget of at least that of this contract in water supplies which was implemented at any moment during the following period:  2019-2022.

- The tenderer has the appropriate equipment for the installation of the water pumps

- The tenderer has the appropriate equipment in order to move, lower and lift the pumps

- The tenderer has the appropriate equipment as the flowmeter for the testing phase

Note:  As it will have to be done with heavy weight equipment employees must be certified for these types of work and be insured by the company for any case of injury or accident.

- Lot n° 2:

The selection criteria for tenderers to lot n° 2 are as follows:

Economic and financial capacity of candidate

- will not be economically dependent on the contracting authority in the event that the contract is awarded to it

- has sufficient financial stability to handle the proposed contract.

- the average annual turnover of the tenderer must exceed the annualised maximum budget of the contract i.e. the maximum budget stated in the contract notice divided by the initial contract duration in years, where this exceeds 1 year (minimum annual turnover requested may not exceed 2 times the estimated annual contract value, except in duly justified cases motivated in the tender dossier);

- Current ratio (current assets/current liabilities) in the last year for which accounts have been closed must be at least 1. In case of a consortium this criterion must be fulfilled by each member.

- the available financial resources of the tenderer must exceed the annualised maximum budget of the contract i.e. the maximum budget stated in the contract notice divided by the initial contract duration in years, where this exceeds 1 year (minimum annual turnover requested may not exceed 2 times the estimated annual contract value, except in duly justified cases motivated in the tender dossier); and

- the financial situation of the tenderer should not be in deficit, considered debts, at the beginning and end of year.

Professional capacity of candidate

- at least 1 professional certificate appropriate to this contract such as electronic engineer

Technical capacity of candidate

- the tenderer has delivered supplies under at least 1 contract with a budget of at least that of this contract in sensors delivery and installation which was implemented at any moment during the following period:  2019-2022.

Award criteria

Price

PARTICIPATION

Requests to participate format and details to be provided

Requests to participate must be submitted using the request to participate form, the format and instructions of which must be strictly observed. The request to participate form is available from the following Internet address:

https://ec.europa.eu/europeaid/prag/document.do?isAnnexes=true

The request to participate must be accompanied by a declaration on honour on exclusion and selection criteria using the template available from the following Internet address:

https://ec.europa.eu/europeaid/prag/document.do?isAnnexes=true

Any documentation (brochure, letter, etc.) sent with a request to participate in addition to what has been requested will not be taken into consideration.

- How requests to participate may be submitted

Paper submission

Requests to participate must be submitted in English exclusively to the contracting authority in a sealed envelope.

- Either by post or by courier service, in which case the evidence shall be constituted by the postmark or the date of the deposit slip, to:

To: Chairman of Procurement Commission

Keshilli i Qarkut Vlore

Pallati i Kultures “Laberia”, kati 3

Vlore

Hours: 8:00 -16:00

OR hand delivered by the participant in person or by an agent directly to the premises of the contracting authority in return for a signed and dated receipt, in which case the evidence shall be constituted by this acknowledgement of receipt, to: 

To: Chairman of Procurement Commission

Keshilli i Qarkut Vlore

Pallati i Kultures “Laberia”, kati 3

Vlore

Hours: 8:00 -16:00

The contract title and publication reference (see contract notice) must be clearly marked on the envelope containing the request to participate and must always be mentioned in all subsequent correspondence with the contracting authority.

Requests to participate submitted by any other means will not be considered.

Deadline for submission of requests to participate

The candidate’s attention is drawn to the fact that there are two different systems for sending Requests to participate: one is by post or private mail service; the other is by hand delivery.

In the first case, the request to participate must be sent before the date and time-limit for submission, as evidenced by the postmark or deposit slip, but in the second case it is the acknowledgment of receipt given at the time of the delivery of the request to participate that will serve as proof.

The deadline for submission of requests to participate can be found in the Contract Notice under IV.2.2. Unless the Time Zone is specified in eTendering, the “Local Time” mentioned under IV.2.2 in the Contract Notice shall be understood as Central European Time (CET) which is the standard time in Brussels.

Any request to participate sent to the contracting authority after this deadline will not be considered. The contracting authority may, for reasons of administrative efficiency, reject any request for participation submitted on time but received, for any reason beyond the contracting authority's control, after the effective date of approval of the short-list report, if accepting requests to participate that were submitted on time but arrived late would considerably delay the evaluation procedure or jeopardise decisions already taken and notified.

Clarifications on the contract notice

N/A

Any request for clarifications must be made in writing through the TED eTendering website accessible from the F&T portal. This concerns request for clarifications about the contract notice and also request for clarifications about the content of the document called “Additional information to the contract notice.” Registration on TED eTendering is required to be able to create and submit a question. Clarifications can be requested by clicking “Create a question” in the Questions & Answers tab at the latest 21 days before the deadline for submission of requests to participate stated at section IV.2.2) of the contract notice.

Clarifications will be published on TED eTendering website at the latest 8 days before the deadline for the submission of requests to participate. The website will be updated regularly and it is the candidate’s responsibility to check for updates and modifications during the submission period.

Outcome of the evaluation

By submitting a request to participate candidates accept to receive notification of the outcome of the procedure by electronic means. Such notification shall be deemed to have been received on the date upon which the contracting authority sends it to the electronic address referred to in the request to participate form.]

Alteration or withdrawal of requests to participate

Candidates may alter or withdraw their requests to participate by written notification prior to the deadline for submission of requests to participate. No requests to participate may be altered after this deadline.

Any such notification of alteration or withdrawal shall be prepared and submitted in accordance with precedent item. The outer envelope (and the relevant inner envelope if used) must be marked ‘Alteration’ or ‘Withdrawal’ as appropriate.

Letter of invitation to tender

Vlore 12.08.2022

Our ref.: PILOT 04/SAVE WATER

Subject: Invitation to tender for < Water Supply Products for the Water Supply System (supply and installation) / LOT 1 and Sensors for the monitoring of Water Supply System (supply and installation) / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

Vlore, Albania

Dear Madam/Sir,

I am pleased to inform you that you are invited to take part in the local open procedure for the above supply contract. The complete tender dossier includes:

- Instructions to tenderers

- Contract notice

- Draft contract and special conditions, including annexes

- Draft contract

- Special conditions

- Annex I:	general conditions

- Annex II + III:	technical specifications + technical offer (to be tailored to the specific project)

- Annex IV:	budget breakdown (model financial offer)

- Annex V:	forms

- Further information

- Administrative compliance grid

- Evaluation grid

- Tender form for a supply contract and Declaration on honour on exclusion and selection criteria (annex A14a)

For full information about procurement procedures please consult the practical guide and its annexes, which can be downloaded from the following web page: http://ec.europa.eu/europeaid/prag/document.do

We look forward to receiving your tender and the accompanying tender guarantee which has to be submitted no later than the submission deadline mentioned in the Contract Notice.

By submitting a tender you accept to receive notification of the outcome of the procedure by electronic means. Such notification shall be deemed to have been received by you on the date upon which the contracting authority sends it to the electronic address you referred to in your offer.

If you decide not to submit a tender, we would be grateful if you could inform us in writing, stating the reasons for your decision.

Yours sincerely,

Regional Council of Vlore

Albania

- A.	INSTRUCTIONS TO TENDERERS

PUBLICATION REF.: < REF: PILOT 04 /SAVE WATER >

By submitting a tender, tenderers fully and unreservedly accept the special and general conditions governing the contract as the sole basis of this tendering procedure, whatever their own conditions of sale may be, which they hereby waive. Tenderers are expected to examine carefully and comply with all instructions, forms, contract provisions and specifications contained in this tender dossier. Failure to submit a tender containing all the required information and documentation within the deadline specified will lead to the rejection of the tender. No account can be taken of any remarks in the tender relating to the tender dossier; remarks may result in the immediate rejection of the tender without further evaluation.

These instructions set out the rules for the submission, selection and implementation of contracts financed under this call for tenders, in conformity with the practical guide (available on the internet at: http://ec.europa.eu/europeaid/prag/document.do).

- 1. Supplies to be provided

- 1.1	The subject of the contract is:

The supply delivery, siting and installation including transportation to the relevant sites, of the following supplies:

Lot 1:

PUMPS AND OTHER SUPPLIES

- 1 item Submersible electric pump. P= 37 kW; H= 210m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel;

- 1 item Centrifugal electric pump. P= 32 kW; H= 150m; Q= 15 l/s; Combined with the electric release panel;

- 1 item Submersible electric pump. P= 26 kW; H= 150m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel;

- 1 item Centrifugal electric pump. P= 132 kW; H= 370m; Q= 15 l/s; Combined with the electric release panel; Ω=1400 no.spins/min

- 2 item Submersible electric pump P= 22 kW; H= 120m; Q= 15 l/s; Diameter of electric motor pump Φ= 4"; Combined with the electric release panel;

- 2 item Submersible electric pump. P= 37 kW; H= 260m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel;

- 2 item Chlorination dosing pumps. Type DMH 252, PVC 45-16 AR 0.18KW 50Hz Ω=1340 no.spins/min PN= 16-20 bar

- 2 item Centrifugal electric pump. P= 7.5 kW; H= 45m; Q= 15 l/s; Combined with the electric release panel;

- 1 item Centrifugal electric pump P= 15 kW; H= 40m; Q= 30 l/s; Combined with the electric release panel;

- 1 item Centrifugal electric pump. P= 37 kW; H= 150m; Q= 15 l/s; Combined with the electric release panel;

- 2 item Submersible electric pump. P= 75 kW; H= 280m; Q= 12 l/s; Diameter of electric motor pump Φ= 8"; Combined with the electric release panel;

- 2 item Vertical Centrifugal Electric Pump. P= 30 kW; H= 160m; Q= 15 l/s; Combined with the electric release panel;

- 1 item Inverter (Allen Brandley PowerFlex type or equivalent with it) 700h series b, 250kW

- 3 item Vacuum Pump (SIHI LEMA type or equivalent with it) 26 51. P= 0.75 - 1.1 kW

- 10 item Sensor, power outage and alarm (Vegaswing type or equivalent with it)   51. SG51XXSGATPM 10-55 volt; transistor PNP; IP67

- 10 item Electric Valve (Danfoss type or equivalent with it) 1/4 " 24 VAC; code EV210B, series 032U1220

- 10 item Inverter blower PowerFlex 700 h series b, Ebompopapst R2E280-AE 52-17; 230V, 50Hz, 1.0A, 225W, 2700 spins/min; with condenser 7μF, 400VDC accompanied by cable and contact

- 5 item Module HIM 20C-C3S, for Inverter (Allen Brandley PowerFlex type or equivalent with it) 700 h series b

- 1 item Converter IFC 100, for water measurements (KROHNE type or equivalent with it)

- 4 item Wheeled mobile water pump with diesel engine

- 4 item Submersible electric pump with switch. Exit Φ= 2"; P= 1.5 kW; H= 1-18m; Q= 1.7-15l/s

- 4 item Diesel motor-generator S= 6 kVA

For more look at the relevant photos at the added document od the tender dossier”  Foto te pompave UK Vlore

The installation will require the below steps and details:

- Installation of Submersible Electric Pump P= 37 kW; H= 210m; Q=12 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P= 32 kW; H= 150m; Q= 15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Submersible Electric Pump P=26 kW;H=150m;Q=12 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P= 132 kW; H= 370m; Q= 15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P=22kW; H=120m; Q=15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Submersible Electric Pump P=37kW; H= 260m; Q=12 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Chlorination dosing pump, GRUNDFOS type of equivalent with it (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump.P=7.5 kW; H=45m; Q= 15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P=15kW; H=40m; Q=30 l/accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P=37kW; H=150m; Q=15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Submersible Electric Pump P=75 kW;H=280m;Q=12 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Vertical Centrifugal Electric Pump P=30kW; H=160m; Q=15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of the Inverter Allen Brandley PowerFlex (or equivalent with it) 700h series b,250kW P= 250 kW; f= 50 Hz; (specialist + operators + auxiliary materials + testing)

- Installation of the vacuum pump SIHI LEMA 26- 51 (or equivalent with it) P= 0.75 - 1.1 kW;(specialist operators)

- Installation of the Sensor, power outage and alarm Vegaswing 51 (or equivalent with it) SG51XXSGATPM 10-55 volt; transistor PNP; IP67;(specialist + operators + auxiliary materials + testing)

- Installation of the Electric Valve Danfoss type 1/4"(or equivalent with it) 24 VAC; kodi EV210B, series 032U1220;(specialist + operators + auxiliary materials + testing)

- Installation of the Inverter blower Power Flextype 700 h serie b type or equivalent with it accompanied by the cable and the contact plug; (specialist + operators + auxiliary materials + testing)

- Installation of the Module HIM 20C-C3S, for Inverter (Allen Brandley PowerFlex 700 h series b type or equivalent with it) ;(specialist + operators + auxiliary materials + testing)

- Installation of the Converter IFC 100, for water measurements (KROHNE type or equivalent with it) ;(specialist + operators + auxiliary materials + testing)

- Installation of the Submersible electric pump with switch Exit Φ= 2”; P= 1.5 kW;H= 1-18m;Q= 1.7-15l/s;(specialist + operators + auxiliary materials + testing)

Lot 2

SENSORS

- 4G/3G AP EU	Meshlium is an IoT gateway that may contain up to 4 different radio interfaces: a WiFi 2.4 GHz (Access Point), a 4G/3G/GPRS/GSM and 2 XBee/RF radios. Meshlium may include Bluetooth, BLE and Wi-Fi radios too for scanning applications.  allow Meshlium to be placed outdoors.  (SUPPLY + SETTING)

- Plugging Sensor base: To ensure the placement of sensor probes. 2-to provide reading of parameters required by sensors.3-to have internal memory SD card.4-to connect to devices with protocol can use Lora Wan, sigfox, 4G, WiFi.5-To ensure data transmission in different formats to data center, as well as be able to connect to the cloud.6-provide replacement and changeable of sensors. To be remoter monitor (SUPPLY + SETTING)

- Conductivity Probe	Sensor connection probes (SUPPLY + SETTING)

- Horizontal liquid level (water)	Sensor + probe (SUPPLY + SETTING)

- Water flow medium	Sensor + probe (SUPPLY + SETTING)

- Ammonium Ion (NH4	Calibration Kit (SUPPLY + SETTING)

- Multi-Ions Calibration Kit (Ammonium, Calcium,	Sensor + probe (SUPPLY + SETTING)

- Chloride, Magnesium, Nitrate, Potassium, Sodium)

- Nitrate Ion 	Sensor + probe (SUPPLY + SETTING)

- Cupric Ion (Cu2+)	Sensor + probe (SUPPLY + SETTING)

- Soil moisture sensor	Sensor + probe (SUPPLY + SETTING)

- Oxidation Reduction Potential Sensor	Sensor + probe (SUPPLY + SETTING)

- Dissolved Oxygen Maintenance Kit	Maintenance Kit (SUPPLY + SETTING)

- Dissolved Oxygen sensor	Sensor + probe (SUPPLY + SETTING)

- Soil/Water temperature Probe	Sensor + probe (SUPPLY + SETTING)

- External solar panel 7V - 500mA 	External solar power supply (SUPPLY + SETTING)

- outdoors USB cable	2m (SUPPLY + SETTING)

- USB-220 V Adapter	 (SUPPLY + SETTING)

- International adapter	 (SUPPLY + SETTING)

- Conductivity Calibration Kit	 (SUPPLY + SETTING)

- pH Calibration Kit	 (SUPPLY + SETTING)

- DO Calibration Solution	 (SUPPLY + SETTING)

- ORP Calibration Solution 	 (SUPPLY + SETTING)

- Internet connection 4 point 12 months	 (SUPPLY + SETTING)

- DO Calibration Solution	 (SUPPLY + SETTING)

- ORP Calibration Solution 	 (SUPPLY + SETTING)

- Turbidity calibration solution, 	 (SUPPLY + SETTING)

- Storage solution for PHEHT probe 	 (SUPPLY + SETTING)

- Sensor protection accessory 	 (SUPPLY + SETTING)

- Prob cable Extensions 1m,1.5m 	 (SUPPLY + SETTING)

- Registration on cloud services 5 users	 (SUPPLY + SETTING)

- Laptop core i7, gen ≥10, SSD 500 GB, 15.6” monitor, MEMORY RAM 16GB, 6 USB ports, power supply eu,lan.WIFI, blutooth

in 2 lots

at Vlore, Albania DDP, and 60 days, in accordance with the contract notice/additional information about the contract notice.

- 1.2	The supplies must comply fully with the technical specifications set out in the tender dossier (technical annex) and conform in all respects with the drawings, quantities, models, samples, measurements and other instructions.

- 1.3	N/A The supplies described under lot No <> must be accompanied by an additional ‘lot’ consisting of spare parts and/or consumables. Neither the unit price, nor the overall price of spare parts will influence the evaluation of the tenders, except where they vary substantially between the tenders received. Lists of spare parts must be drawn up by tenderers on the basis of their professional experience and the expected places of use; they must show the unit prices of the parts, calculated as specified in Article 11 (below). The contracting authority reserves the right to alter the list of spare parts; any changes will appear in the contract.

- 1.4 	Tenderers are not authorised to tender for a variant solution in addition to the present tender.

- 2. Timetable

|  | DATE | TIME |
| --- | --- | --- |
| Clarification meeting / site visit (if any) | 17.08.2022 | 12:00 |
| Deadline for requesting clarifications from the contracting authority | Date 21 days before deadline for tenders indicated in the Contract notice | 08:00-16:00 |
| Last date on which clarifications are issued by the contracting authority | Date 8 days before deadline for submission of tenders indicated in the Contract notice | - |
| Deadline for submission of tenders | 15.09.2022 (As indicated in the Contract notice) | Up to 16:00 |
| Tender opening session | 19/09/2022 As indicated in the Contract Notice (IV.2.7) | 10:00 |
| Notification of award to the successful tenderer | 04.10.2022 * | Up to 16:00 |
| Signature of the contract | 07.10.2022 – lot 1 10.10.2022 – lot 2 | Up to 16:00 |

* Provisional date

- 3. Participation

- 3.1.	The eligibility requirements detailed in the Additional information about the contract notice (Annex A5f) or, if applicable, in the Contract Notice (C2), apply to all members of a joint venture/consortium and all subcontractors, as well as to all entities upon whose capacity the tenderer relies for the selection criteria. Every tenderer, member of a joint venture/consortium, every capacity-providing entity, every subcontractor must certify that they meet these conditions. They must prove their eligibility by a document dated less than one year earlier than the deadline for submitting tenders, drawn up in accordance with their national law or practice or by copies of the original documents stating the constitution and/or legal status and the place of registration and/or statutory seat and, if it is different, the place of central administration. The contracting authority may accept other satisfactory evidence that these conditions are met.

- 3.2.	Natural or legal persons are not entitled to participate in this tender procedure or be awarded a contract if they are in any of the situations mentioned in Sections 2.4. (EU restrictive measures), 2.6.10.1. (exclusion criteria) or 2.6.10.1.2. (rejection from a procedure) of the practical guide. Should they do so, their tender will be considered unsuitable or irregular respectively. In the cases listed in Section 2.6.10.1. of the practical guide tenderers may also be excluded from EU financed procedures and be subject to financial penalties up to 10 % of the total value of the contract in accordance with the Financial Regulation in force. This information may be published on the Commission website in accordance with the Financial Regulation in force. Tenderers must provide declarations on honour that they are not in any of these exclusion situations. Such declarations must also be submitted by all the members of a joint venture/consortium, by any sub-contractor and by any capacity providing entities. Tenderers who make false declarations may also incur financial penalties and exclusion in accordance with the Financial Regulation in force. Their tender will be considered irregular.

- The exclusion situations referred to above also apply to all members of a joint venture/consortium, all subcontractors and all suppliers to tenderers, as well as to all entities upon whose capacity the tenderer relies for the selection criteria. In cases of doubt over declarations, the contracting authority will request documentary evidence that subcontractors and/or capacity providing entities are not in a situation that excludes them.

- 3.3.	To be eligible to take part in this tender procedure, tenderers must prove to the satisfaction of the contracting authority that they comply with the necessary legal, technical and financial requirements and have the means to carry out the contract effectively.

- 3.4.	Subcontracting is allowed.  The tenderer and, where applicable, entities on whose capacities it has relied with regard to criteria relating to the economic and financial capacity shall be jointly liable for the performance of the contract.

- To be inserted only in case the contracting authority identifies certain critical activities cannot be subcontracted. WARNING: these critical tasks identified by the contracting authority must be strictly linked to siting and/or installation operations The contracting authority requires that the following critical tasks be performed directly by the tenderer itself or, where the tender is submitted by a group of economic operators, a participant in the group:

- Employees who will work with the installation of pumps, all of which are heavy weight must be certified for this type of work

- Employees who will work with the installation must be insured by the company for any case of damage or accident

- since it is foreseen to install over 15 pumps the company must have at its disposal at least 2-3 working groups to conclude the contract within the deadline, November 30, 2022

- 4. Origin

4.1

For commitments financed by a basic act under the MFF 2021-2027:

All supplies under this contract may originate in any country.

For commitments financed by a basic act under the MFF 2014-2020:

- Unless otherwise provided in the contract or below all goods purchased under the contract must originate in a Member State of the European Union or in a country or territory of the regions covered and/or authorised by the specific instruments applicable to the programme specified in the Additional information about the contract notice (Annex A5f). For these purposes, ‘origin’ means the place where the goods are mined, grown, produced or manufactured and/or from which services are provided. The origin of the goods must be determined according to the relevant international agreements (notably WTO agreements), which are reflected in EU legislation on rules of origin for customs purposes: The Customs Code (Council Regulation (EEC) No 2913/92) in particular its Articles 22 to 246 thereof, and the Code's implementing provisions (Commission Regulation (EEC) No 2454/93. [EDF: Goods originating in the EU include goods originating in the Overseas Countries and Territories.]

General budget of the Union for calls where the CIR applies and 10th EDF/11th EDF:

If the estimated intrinsic value of the products is above or equal to EUR 100 000: All supplies under this contract must originate in one or more of the above countries.

If the estimated intrinsic value of the products (of the tender procedure as a whole or if divided into lots, per lot) is below EUR 100 000: All supplies under this contract may originate from any country.

- Tenderers must provide an undertaking signed by their representative certifying compliance with this requirement. The tenderer is obliged to verify that the provided information is correct. Otherwise, the tenderer risks to be excluded because of negligently misrepresenting information. For more details, see Section 2.3.5. of the practical guide.

Also, see Legal basis, eligibility and rules of origin of Additional Information about the Contract Notice of this tender dossier.

- 4.2	When submitting tenders, tenderers must state expressly that all the goods meet the requirements concerning origin and must state the countries of origin. They may be asked to provide additional information in this connection.

- 5. Type of contract

- Lump sum

- 6. Currency

- Tenders must be presented in LEK.

- 7. Lots

- 7.1	The tenderer may submit a tender for all of the lots.

- 7.2	Each lot will form a separate contract and the quantities indicated for different lots will be indivisible. The tenderer must offer the whole of the quantity or quantities indicated for each lot. Under no circumstances must tenders be considered for part of the quantities required. If the tenderer is awarded more than one lot, a single contract may be concluded covering all those lots.

- 7.3	A tenderer may include in its tender the overall discount it would grant in the event of some or all of the lots for which it has submitted a tender being awarded. The discount should be clearly indicated for each lot in such a way that it can be announced during the public tender opening session.

- 7.4	Contracts will be awarded lot by lot, but the contracting authority may select the most favourable overall solution after taking account of any discounts offered.]

- 8. Period of validity

- 8.1	Tenderers will be bound by their tenders for a period of 90 days from the deadline for the submission of tenders.

- 8.2	In exceptional cases and prior to the expiry of the original tender validity period, the contracting authority may ask tenderers in writing to extend this period by 40 days. Such requests and the responses to them must be made in writing. Tenderers that agree to do so will not be permitted to modify their tenders and they are bound to extend the validity of their tender guarantees for the revised period of validity of the tender. If they refuse, without forfeiture of their tender guarantees, their participation in the tender procedure will be terminated. In case the contracting authority is required to obtain the recommendation of the panel referred to in Section 2.6.10.1.1. of the practical guide, the contracting authority may, before the validity period expires, request an extension of the validity of the tenders up to the adoption of that recommendation.

8.3	The successful tenderer will be bound by its tender for a further period of 60 days. The further period is added to the validity period of the tender irrespective of the date of notification.

- 9. Language of tenders

- 9.1	The tenders, all correspondence and documents related to the tender exchanged by the tenderer and the contracting authority must be written in the language of the procedure, which is English.

- If the supporting documents are not written in one of the official languages of the European Union, a translation into the language of the call for tender must be attached. Where the documents are in an official language of the European Union other than English, it is strongly recommended to provide a translation into English, to facilitate evaluation of the documents.

- 10. Submission of tenders

10.1 Paper submission:

- Tenders must be sent to the contracting authority before the deadline specified in Contract Notice. They must include all the documents specified in point 11 of these Instructions and be sent to the following address:

Keshilli i Qarkut Vlore

Pallati i Kultures “Laberia”, kati 3

Vlore

Hours: 8:00 -16:00

If the tenders are hand delivered they should be delivered to the following address:

Keshilli i Qarkut Vlore

Pallati i Kultures “Laberia”, kati 3

Vlore

Hours: 8:00 -16:00>

Chairman of Procurement Commission

Tenders must comply with the following conditions:

- 10.2	All tenders must be submitted in one original, marked ‘original’, and 3 (with double side printing, degradable material for folders, presentation, etc…) copies signed in the same way as the original and marked ‘copy’.

- 10.3	The tenders should be submitted:

- (a) either by post or by courier service, in which case the evidence shall be constituted by the postmark or the date of the deposit slip

- (b) or by hand-delivery to the premises of the contracting authority by the participant in person or by an agent, in which case the evidence shall be constituted by the acknowledgment of receipt.

- The contracting authority may, for reasons of administrative efficiency, reject any application or tender submitted on time to the postal service but received, for any reason beyond the contracting authority's control, after the effective date of approval of the short-list report or of the evaluation report, if accepting applications or tenders that were submitted on time but arrived late would considerably delay the evaluation procedure or jeopardise decisions already taken and notified.

- 10.4	All tenders, including annexes and all supporting documents, must be submitted in a sealed envelope bearing only:

- a)	the above address;

- b)	the reference code of this tender procedure PILOT 04/SAVE WATER;

- c)	the number of the lot(s) tendered for;

- d)	the words ‘Not to be opened before the tender opening session’ in the language of the tender dossier and <Të mos hapet para seancës së hapjes së tenderit>.

- e)	the name of the tenderer.

- The technical and financial offers must be placed together in a sealed envelope. The envelope should then be placed in another single sealed envelope/package, unless their volume requires a separate submission for each lot.

- 11. Content of tenders

- Failure to fulfil the below requirements will constitute an irregularity and may result in rejection of the tender. All tenders submitted must comply with the requirements in the tender dossier and comprise:

- Part 1: Technical offer:

- a detailed description of the supplies tendered in conformity with the technical specifications, including any documentation required

The technical offer should be presented as per template (Annex II+III*, Contractor’s technical offer) adding separate sheets for details if necessary.

- Part 2: Financial offer:

- A financial offer calculated on a DDP basis for the supplies tendered, including

  - financial proposal for transportation, siting and installation

This financial offer should be presented as per template (Annex IV*, Budget breakdown), adding separate sheets for details if necessary.

In case of doubt about the applicable VAT system, it is the tenderer's responsibility to contact his or her national authorities to clarify the way in which the European Union is exempt from VAT.

Part 3: Documentation:

To be supplied using the templates attached*:

- The "Tender form for a supply contract", together with Annex 1 "Declaration on honour on exclusion criteria and selection criteria", both duly completed, which includes the tenderer’s declaration, point 7, (from each member if a consortium).

- The details of the bank account into which payments should be made (financial identification form – document c4o1_fif_en) (tenderers that have already signed another contract with the European Commission, may provide their financial identification form number instead of the financial identification form, or a copy of the financial identification form provided on that occasion, if no change has occurred in the meantime.)

- The legal entity file (document c4o2_lefind_en) and the supporting documents (tenderers that have already signed another contract with the European Commission, may provide their legal entity number instead of the legal entity sheet and supporting documents, or a copy of the legal entity sheet provided on that occasion, if no change in legal status has occurred in the meantime).

To be supplied in free-text format:

- A description of the warranty conditions, which must be in accordance with the conditions laid down in Article 32 of the general conditions.

- A description of the organisation of the commercial warranty tendered in accordance with the conditions laid down in Article 32 of the special conditions

- If the contract is financed by a basic act under the Multiannual Financial Framework for the years 2014-2020 (contracts/lots above EUR 100 000 under CIR and independently of the value for other instruments) A statement by the tenderer attesting the origin of the supplies tendered (or other proofs of origin).

- Duly authorised signature: an official document (statutes, power of attorney, notary statement, etc.) proving that the person who signs on behalf of the company, joint venture or consortium is duly authorised to do so.

- The contractor is able to set up a temporary construction site for the installation process of equipment for Lot 1

- Remarks:

Tenderers are requested to follow this order of presentation.

Annex* refers to templates attached to the tender dossier. These templates are also available on: http://ec.europa.eu/europeaid/prag/annexes.do?group=C

- 12. Taxes and other charges

- The applicable tax and customs arrangements are the following:

The European Commission and Albania have agreed in FINANCING AGREEMENT for Interreg IPA cross-border cooperation programme Greece-Albania 2014-2020 CCI 2014TC16I5CB010 to fully exonerate the following taxes VAT /TVSH.

For more details on taxes, customs, duties and other fiscal charges see Title IV, Article 28 of the Framework Agreement between the Republic of Albania represented by the Government of the Republic of Albania and the European Commission on the Arrangements for Implementation of Union Financial Assistance to the Republic of Albania under the Instrument for Pre-accession (IPA II).

- 13. Additional information before the deadline for submission of tenders

Tenderers may submit questions in writing to the following address up to local open procedure: 21 days before the deadline for submission of tenders, specifying the publication reference and the contract title:

Keshilli i Qarkut Vlore

Pallati i Kultures “Laberia”, kati 3

Vlore

Email: info@qarkuvlore.gov.al

To: The Manager of the Project SAVE WATER

Any clarification of the tender dossier will be communicated simultaneously in writing to all tenderers at the latest 8 days before the deadline for submitting tenders.

Any prospective tenderers seeking to arrange individual meetings with either the contracting authority and/or the European Commission during the tender period may be excluded from the tender procedure.

- 14. Clarification meeting / site visit

  - A clarification meeting / site visit will be held on 17.08.2022 at 12:00  (time zone of the location of the site)  at Këshilli i Qarkut Vlorë Pallati i Kultures “Laberia”, kati 3, Vlore to answer any questions on the tender dossier which have been forwarded in writing or are raised at the meeting. Minutes will be taken during the meeting and these will be communicated — together with any clarifications in response to written requests which are not addressed during the meeting — at the latest 8 calendar days before the deadline for submission of tenders. No further clarification will be provided after this date. All the costs of attending this meeting will be borne by the tenderers.

  - Other than this site visit for all prospective tenderers, no visits by individual prospective tenderers can be organised during the tender period.]

- Alteration or withdrawal of tenders

- 15.1	Paper submission: Tenderers may alter or withdraw their tenders by written notification prior to the deadline for submission of tenders. No tender may be altered after this deadline. Withdrawals must be unconditional and will end all participation in the tender procedure.

- Any such notification of alteration or withdrawal must be prepared and submitted in accordance with Section 10. The outer envelope must be marked ‘Alteration’ or ‘Withdrawal’ as appropriate.

- 15.2	No tender may be withdrawn in the interval between the deadline for submission of tenders.1 and the expiry of the tender validity period. Withdrawal of a tender during this interval may result in forfeiture of the tender guarantee.

- 16. Costs of preparing tenders

No costs incurred by the tenderer in preparing and submitting the tender are reimbursable. All such costs will be borne by the tenderer.

- 17. Ownership of tenders

The contracting authority retains ownership of all tenders received under this tender procedure. Consequently, tenderers have no right to have their tenders returned to them.

- 18. Joint venture or consortium

- 18.1	If a tenderer is a joint venture or consortium of two or more persons, the tender must be a single one with the object of securing a single contract, each person must sign the tender and will be jointly and severally liable for the tender and any contract. Those persons must designate one of their members to act as leader with authority to bind the joint venture or consortium. The composition of the joint venture or consortium must not be altered without the prior written consent of the contracting authority.

- 18.2	The tender may be signed by the representative of the joint venture or consortium only if it has been expressly so authorised in writing by the members of the joint venture or consortium, and the authorising contract, notarial act or deed must be submitted to the contracting authority in accordance with point 11 of these instructions to tenderers. All signatures to the authorising instrument must be certified in accordance with the national laws and regulations of each party comprising the joint venture or consortium together with the powers of attorney establishing, in writing, that the signatories to the tender are empowered to enter into commitments on behalf of the members of the joint venture or consortium. Each member of such joint venture or consortium must provide the proof required under Article 3.5 as if it, itself, were the tenderer.

- 19. Opening of tenders

- 19.1	The purpose of the opening session is to check whether the tenders have been submitted in accordance with the submission requirements of the call for tenders.

For the open procedure.

- 19.2	The date and venue of the tender opening session is indicated in Section IV.2.7 of the Contract Notice.

- The committee will draw up minutes of the meeting, which will be available on request.

In the case that at the date of the opening session some tenders have not been delivered to the contracting authority but their representatives can show evidence that it has been sent on time, the contracting authority will allow them to participate in the first opening session and inform all representatives of the tenderers that a second opening session will be organised.

19.3	At the tender opening, the tenderers’ names, the tender prices, any discount offered, written notifications of alteration and withdrawal, the presence of the requisite tender guarantee (if required) and such other information as the contracting authority may consider appropriate may be announced.

- 19.4	After the public opening of the tenders, no information relating to the examination, clarification, evaluation of tenders, or recommendations concerning the award of the contract can be disclosed until after the contract has been awarded.

- 19.5	Any attempt by tenderers to influence the evaluation committee in the process of examination, clarification, evaluation and comparison of tenders, to obtain information on how the procedure is progressing or to influence the contracting authority in its decision concerning the award of the contract will result in the immediate rejection of their tenders.

- 19.6	All tenders received after the deadline for submission specified in the contract notice or these instructions will be kept by the contracting authority. The associated guarantees will be returned to the tenderers. No liability can be accepted for late delivery of tenders. Late tenders will be rejected and will not be evaluated.

- 20. Evaluation of tenders

- 20.1	Examination of the administrative conformity of tenders

- The aim at this stage is to check that tenders comply with the essential requirements of the tender dossier. A tender is deemed to comply if it satisfies all the conditions, procedures and specifications in the tender dossier without substantially departing from or attaching restrictions to them.

- Substantial departures or restrictions are those which affect the scope, quality or execution of the contract, differ widely from the terms of the tender dossier, limit the rights of the contracting authority or the tenderer’s obligations under the contract or distort competition for tenderers whose tenders do comply. Decisions to the effect that a tender is not administratively compliant must be duly justified in the evaluation minutes.

- If a tender does not comply with the tender dossier, it will be rejected immediately and may not subsequently be made to comply by correcting it or withdrawing the departure or restriction.

- 20.2	Technical evaluation

- After analysing the tenders deemed to comply in administrative terms, the evaluation committee will rule on the technical admissibility of each tender, classifying it as technically compliant or non-compliant.

- The minimum qualifications required (see selection criteria in the additional information about the contract notice are to be evaluated at the start of this stage.

- Where contracts include after-sales service and/or training, the technical quality of such services will also be evaluated by using yes/no criteria as specified in the tender dossier.

- 20.3	In the interests of transparency and equal treatment and to facilitate the examination and evaluation of tenders, the evaluation committee may ask each tenderer individually for clarification of its tender including breakdowns of prices, within a reasonable time limit to be fixed by the evaluation committee. The request for clarification and the response must be in writing, but no change in the price or substance of the tender may be sought, offered or permitted except as required to confirm the correction of arithmetical errors discovered during the evaluation of tenders pursuant to Article 20.4. Any such request for clarification must not distort competition. Decisions to the effect that a tender is not technically compliant must be duly justified in the evaluation minutes.

- 20.4	Financial evaluation

a)	Tenders found to be technically compliant will be checked for any arithmetical errors in computation and summation. Errors will be corrected by the evaluation committee as follows:

- -	where there is a discrepancy between amounts in figures and in words, the amount in words will be the amount taken into account;

- -	except for lump-sum contracts, where there is a discrepancy between a unit price and the total amount derived from the multiplication of the unit price and the quantity, the unit price as quoted will be the price taken into account.

b)	Amounts corrected in this way will be binding on the tenderer. If the tenderer does not accept them, its tender will be rejected.

c) Unless specified otherwise, the purpose of the financial evaluation process is to identify the tenderer offering the lowest price. Where specified in the technical specifications, the evaluation of tenders may take into account not only the acquisition costs but, to the extent relevant, costs borne over the life cycle of the supplies (such as for instance maintenance costs and operating costs), in line with the technical specifications. In such case, the contracting authority will examine in detail all the information supplied by the tenderers and will formulate its judgment on the basis of the lowest total cost, including additional costs.

- 20.5	Variant solutions

Variant solutions will not be taken into consideration.

- 20.6	Award criteria

- To be used in all cases except where a supply contract includes particularly significant ancillary services (see below and practical guide 4.3.3.): The sole award criterion will be the price. The contract will be awarded to the lowest compliant tender.

  - Documentary evidence for exclusion and selection criteria

For tenders below EUR 300 000, the contracting authority may, if it has doubts about whether the tenderer to whom the contract is to be awarded is in one of the situations leading to exclusion, require the tenderer to provide the evidence on exclusion criteria: At any time during the procurement procedure and before the award of the contract, the contracting authority may request documentary evidence on compliance with the exclusion criteria set out in these instructions.

For tenders below EUR 300 000, the contracting authority may, depending on its assessment of the risks, decide not to require proof for selection criteria, but then no pre-financing must be made, see Section 2.6.11. of the practical guide: No documentary evidence of the selection criteria shall be submitted but no pre-financing will be granted.

For tenders above EUR 300 000 and for tenders below EUR 300 000 when the Contracting Authority decided to request documentary for exclusion and evidence criteria:

At any time during the procurement procedure and before the award of the contract, the contracting authority may request documentary evidence on compliance with the exclusion criteria and selection criteria (financial, economic, technical and professional capacity) set out in these instructions. Please note that a request for evidence in no way implies that the tenderer has been successful. All tenderers are invited to prepare in advance the documents related to the evidence, since they may be requested to provide such evidence within a short deadline. In any event, the tenderer proposed by the evaluation committee for the award of the contract, will be requested to provide such evidence at short notice.

When requested, regarding the exclusion criteria, the tenderers should be able to provide the documentary proof or statements required under the law of the country in which the company (or, for consortia, each of the companies) is established, to show that it does not fall into any of the exclusion situations listed in Section 2.6.10.1. of the practical guide.

- This evidence, documents or statements must be dated, no more than one year before the date of submission of the tender.

The above-mentioned documents must be submitted for every member of a joint venture/consortium, all subcontractors and every capacity providing entity.

- The contracting authority may waive the obligation of any tenderer to submit the documentary evidence referred to above if such evidence has already been submitted for the purposes of another procurement procedure, provided that the issue date of the documents does not exceed one year and that they are still valid. In this case, the tenderer must declare on his/her honour that the documentary evidence has already been provided in a previous procurement procedure and confirm that his/her situation has not changed.

- Where the documentary evidence submitted is in an official language of the European Union other than the one of the procedure, it is strongly recommended to provide a translation into the language of the procedure, in order to facilitate the evaluation of the documents.

- Failure to provide valid documentary evidence at the request and within the deadline set by the Contracting Authority shall lead to the rejection of the tender for the award of the contract, unless the tenderer can justify the failure on the grounds of material impossibility.

If the successful tenderer fails to provide this documentary proof or statement or if the successful tenderer is found to have provided false information, the award will be considered null and void. In this case, the contracting authority may award the tender to the next lowest tenderer or cancel the tender procedure.

21.	Notification of award

By submitting a tender, each tenderer accepts to receive notification of the outcome of the procedure by electronic means. Such notification shall be deemed to have been received on the date upon which the contracting authority sends it to the electronic address referred to in the offer.

The contracting authority will inform all tenderers simultaneously and individually of the award decision. The tender guarantees of the unsuccessful tenderers will be released once the contract is signed. The successful tenderer will be informed in writing that its tender has been accepted (notification of award).

- 22.	Signature of the contract and performance guarantee

- 22.1	The contracting authority reserves the right to vary quantities specified in the tender by +/- 100 % at the time of contracting and during the validity of the contract. The total value of the supplies may not, as a result of the variation rise or fall by more than 25 % of the original financial offer in the tender. The unit prices quoted in the tender shall be used.

- 22.2	Within 30 days of receipt of the contract signed by the contracting authority, the selected tenderer must sign and date the contract and return it, with the performance guarantee (if applicable), to the contracting authority. On signing the contract, the successful tenderer will become the contractor and the contract will enter into force.

- 22.3	If it fails to sign and return the contract and any financial guarantee required within 30 days after receipt of notification, the contracting authority may consider the acceptance of the tender to be cancelled without prejudice to the contracting authority’s right to seize the guarantee, claim compensation or pursue any other remedy in respect of such failure, and the successful tenderer will have no claim whatsoever on the contracting authority.

- 22.4	The performance guarantee referred to in the general conditions is set at < insert percentage between 5 and 10>% of the amount of the contract The performance guarantee must be presented in the form specified in the annex to the tender dossier. It will be released within 45 days of the issue of the final acceptance certificate by the contracting authority, except for the proportion assigned to after-sales service. For contracts of EUR 150 000 or below, on the basis of objective criteria such as the type and value of the contract, the contracting authority may decide not to require such a guarantee.

- 23.	Tender guarantee

- No tender guarantee is required.

- 24. Ethics clauses and code of conduct

- 24.1	Absence of conflict of interest

The tenderer must not be affected by any conflict of interest and must have no equivalent relation in that respect with other tenderers or parties involved in the project. Any attempt by a tenderer to obtain confidential information, enter into unlawful agreements with competitors or influence the evaluation committee or the contracting authority during the process of examining, clarifying, evaluating and comparing tenders will lead to the rejection of its tender and may result in administrative penalties according to the Financial Regulation in force.

- 24.2	Respect for human rights as well as environmental legislation and core labour standards

The tenderer and its personnel must comply with human rights and applicable data protection rules. In particular and in accordance with the applicable basic act, tenderers and applicants who have been awarded contracts must comply with the environmental legislation including multilateral environmental agreements, and with the core labour standards as applicable and as defined in the relevant International Labour Organisation conventions (such as the conventions on freedom of association and collective bargaining; elimination of forced and compulsory labour; abolition of child labour).

Zero tolerance for sexual exploitation, abuse and harassment:

The European Commission applies a policy of 'zero tolerance' in relation to all wrongful conduct which has an impact on the professional credibility of the tenderer.

Physical abuse or punishment, or threats of physical abuse, sexual abuse or exploitation, harassment and verbal abuse, as well as other forms of intimidation shall be prohibited.

- 24.3 Anti-corruption and anti-bribery

The tenderer shall comply with all applicable laws and regulations and codes relating to anti-bribery and anti-corruption. The European Commission reserves the right to suspend or cancel project financing if corrupt practices of any kind are discovered at any stage of the award process or during the execution of a contract and if the contracting authority fails to take all appropriate measures to remedy the situation. For the purposes of this provision, ‘corrupt practices’ are the offer of a bribe, gift, gratuity or commission to any person as an inducement or reward for performing or refraining from any act relating to the award of a contract or execution of a contract already concluded with the contracting authority.

- 24.4	Unusual commercial expenses

Tenders will be rejected or contracts terminated if it emerges that the award or execution of a contract has given rise to unusual commercial expenses. Such unusual commercial expenses are commissions not mentioned in the main contract or not stemming from a properly concluded contract referring to the main contract, commissions not paid in return for any actual and legitimate service, commissions remitted to a tax haven, commissions paid to a payee who is not clearly identified or commissions paid to a company which has every appearance of being a front company.

Contractors found to have paid unusual commercial expenses on projects funded by the European Union are liable, depending on the seriousness of the facts observed, to have their contracts terminated or to be permanently excluded from receiving EU funds.

- 24.5	Breach of obligations, irregularities or fraud

The contracting authority reserves the right to suspend or cancel the procedure, where the award procedure proves to have been subject to breach of obligations, irregularities or fraud. If breach of obligations, irregularities or fraud are discovered after the award of the contract, the contracting authority may refrain from concluding the contract.

- 25.	Cancellation of the tender procedure

If a tender procedure is cancelled, tenderers will be notified by the contracting authority.

If the tender procedure is cancelled before the tender opening session the sealed envelopes will be returned, unopened, to the tenderers.

Cancellation may occur, for example, if:

- the tender procedure has been unsuccessful, namely where no suitable, qualitatively or financially acceptable tender has been received or there has been no valid response at all;

- the economic or technical parameters of the project have changed fundamentally;

- exceptional circumstances or force majeure render normal implementation of the project impossible;

- all technically acceptable tenders exceed the financial resources available;

- there have been breach of obligations, irregularities or frauds in the procedure, in particular where these have prevented fair competition;

- the award is not in compliance with sound financial management, i.e. does not respect the principles of economy, efficiency and effectiveness (e.g. the price proposed by the tenderer to whom the contract is to be awarded is objectively disproportionate with regard to the price of the market.

In no event will the contracting authority be liable for any damages whatsoever including, without limitation, damages for loss of profits, in any way connected with the cancellation of a tender procedure even if the contracting authority has been advised of the possibility of damages. The publication of a contract notice does not commit the contracting authority to implement the programme or project announced.

- 26. 	Appeals

Tenderers believing that they have been harmed by an error or irregularity during the award process may file a complaint. See Section 2.12. of the practical guide.

27. Data Protection

Processing of personal data related to this tender procedure by the contracting authority takes place in accordance with the national legislation of the state of the contracting authority and with the provisions of the respective financing agreement.

The tender procedure and the contract relate to an external action funded by the EU, represented by the European Commission. If processing your reply to the invitation to tender involves transfer of personal data (such as names, contact details and CVs) to the European Commission, they will be processed solely for the purposes of the monitoring of the procurement procedure and of the implementation of the contract by the Commission, for the latter to comply with its obligations under the applicable legislative framework and under the financing agreement concluded between the EU and the Partner Country without prejudice to possible transmission to the bodies in charge of monitoring or inspection tasks in application of EU law. For the part of the data transferred by the contracting authority to the European Commission, the controller for the processing of personal data carried out within the Commission is

For any other DG please add the function of your controller

Details concerning processing of your personal data by the Commission are available on the privacy statement at:

http://ec.europa.eu/europeaid/prag/annexes.do?chapterTitleCode=A

In cases where you are processing personal data in the context of participation to a tender (e.g. CVs of both key and technical experts) and/or implementation of a contract (e.g. replacement of experts) you shall accordingly inform the data subjects of the possible transmission of their data to EU institutions and bodies and communicate the above-mentioned privacy statement to them.

- 28.	Early detection and exclusion system

The tenderers and, if they are legal entities, persons who have powers of representation, decision-making or control over them, are informed that, should they be in one of the situations of early detection or exclusion, their personal details (name, given name if natural person, address, legal form and name and given name of the persons with powers of representation, decision-making or control, if legal person) may be registered in the early detection and exclusion system, and communicated to the persons and entities listed in the above-mentioned decision, in relation to the award or the execution of a procurement contract

- DRAFT CONTRACT

SUPPLY CONTRACT FOR EUROPEAN

UNION EXTERNAL ACTIONS

No  PILOT 04/SAVE WATER / Lot 1

financed from General budget of the Union

in the frame work of Interreg IPA II cross-border cooperation programme Greece - Albania 2014-2020

Keshilli i Qarkut Vlore, Pallati i Kultures “Laberia”, kati 3, Vlore, aLBANIA

(‘The contracting authority’),

of the one part,

and

<Full official name of contractor>

[<Legal status/title>]

[<Official registration number>]

<Full official address>

[<VAT number>], (‘the contractor’)

of the other part,

have agreed as follows:

- PROJECT Improving water management and supply infrastructure via smart technologies, policies and tools SAVE-WATER

- CONTRACT TITLE Water Supply Products for the Water Supply System (supply and installation) / LOT 1 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

- Identification number < PILOT 04/SAVE WATER >

- Article 1	Subject

  - The subject of the contract shall be:

the supply, delivery, unloading, siting and installation, commissioning, of the following supplies for the lot no 1:

PUMPS AND OTHER SUPPLIES

- 1 item Submersible electric pump. P= 37 kW; H= 210m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel;

- 1 item Centrifugal electric pump. P= 32 kW; H= 150m; Q= 15 l/s; Combined with the electric release panel;

- 1 item Submersible electric pump. P= 26 kW; H= 150m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel;

- 1 item Centrifugal electric pump. P= 132 kW; H= 370m; Q= 15 l/s; Combined with the electric release panel; Ω=1400 no.spins/min

- 2 item Submersible electric pump P= 22 kW; H= 120m; Q= 15 l/s; Diameter of electric motor pump Φ= 4"; Combined with the electric release panel;

- 2 item Submersible electric pump. P= 37 kW; H= 260m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel;

- 2 item Chlorination dosing pumps. Type DMH 252, PVC 45-16 AR 0.18KW 50Hz Ω=1340 no.spins/min PN= 16-20 bar

- 2 item Centrifugal electric pump. P= 7.5 kW; H= 45m; Q= 15 l/s; Combined with the electric release panel;

- 1 item Centrifugal electric pump P= 15 kW; H= 40m; Q= 30 l/s; Combined with the electric release panel;

- 1 item Centrifugal electric pump. P= 37 kW; H= 150m; Q= 15 l/s; Combined with the electric release panel;

- 2 item Submersible electric pump. P= 75 kW; H= 280m; Q= 12 l/s; Diameter of electric motor pump Φ= 8"; Combined with the electric release panel;

- 2 item Vertical Centrifugal Electric Pump. P= 30 kW; H= 160m; Q= 15 l/s; Combined with the electric release panel;

- 1 item Inverter (Allen Brandley PowerFlex type or equivalent with it) 700h series b, 250kW

- 3 item Vacuum Pump (SIHI LEMA type or equivalent with it) 26 51. P= 0.75 - 1.1 kW

- 10 item Sensor, power outage and alarm (Vegaswing type or equivalent with it)   51. SG51XXSGATPM 10-55 volt; transistor PNP; IP67

- 10 item Electric Valve (Danfoss type or equivalent with it) 1/4 " 24 VAC; code EV210B, series 032U1220

- 10 item Inverter blower PowerFlex 700 h series b, Ebompopapst R2E280-AE 52-17; 230V, 50Hz, 1.0A, 225W, 2700 spins/min; with condenser 7μF, 400VDC accompanied by cable and contact

- 5 item Module HIM 20C-C3S, for Inverter (Allen Brandley PowerFlex type or equivalent with it) 700 h series b

- 1 item Converter IFC 100, for water measurements (KROHNE type or equivalent with it)

- 4 item Wheeled mobile water pump with diesel engine

- 4 item Submersible electric pump with switch. Exit Φ= 2"; P= 1.5 kW; H= 1-18m; Q= 1.7-15l/s

- 4 item Diesel motor-generator S= 6 kVA

The installation will require the below steps and details:

- Installation of Submersible Electric Pump P= 37 kW; H= 210m; Q=12 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P= 32 kW; H= 150m; Q= 15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Submersible Electric Pump P=26 kW;H=150m;Q=12 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P=22kW; H=120m; Q=15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Submersible Electric Pump P=37kW; H= 260m; Q=12 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump.P=7.5 kW; H=45m; Q= 15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P=15kW; H=40m; Q=30 l/accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Centrifugal Electric Pump P=37kW; H=150m; Q=15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Submersible Electric Pump P=75 kW;H=280m;Q=12 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of Vertical Centrifugal Electric Pump P=30kW; H=160m; Q=15 l/s; Accompanied by the electrical release panel (specialist + operators + auxiliary materials + testing)

- Installation of the Inverter Allen Brandley PowerFlex (or equivalent with it) 700h series b,250kW P= 250 kW; f= 50 Hz; (specialist + operators + auxiliary materials + testing)

- Installation of the vacuum pump SIHI LEMA 26- 51 (or equivalent with it) P= 0.75 - 1.1 kW;(specialist operators)

- Installation of the Sensor, power outage and alarm Vegaswing 51 (or equivalent with it) SG51XXSGATPM 10-55 volt; transistor PNP; IP67;(specialist + operators + auxiliary materials + testing)

- Installation of the Electric Valve Danfoss type 1/4"(or equivalent with it) 24 VAC; kodi EV210B, series 032U1220;(specialist + operators + auxiliary materials + testing)

- Installation of the Inverter blower Power Flextype 700 h serie b type or equivalent with it accompanied by the cable and the contact plug; (specialist + operators + auxiliary materials + testing)

- Installation of the Module HIM 20C-C3S, for Inverter (Allen Brandley PowerFlex 700 h series b type or equivalent with it) ;(specialist + operators + auxiliary materials + testing)

- Installation of the Converter IFC 100, for water measurements (KROHNE type or equivalent with it) ;(specialist + operators + auxiliary materials + testing)

- Installation of the Submersible electric pump with switch Exit Φ= 2”; P= 1.5 kW;H= 1-18m;Q= 1.7-15l/s;(specialist + operators + auxiliary materials + testing)

The place of acceptance of the supplies shall be in Vlora city, Albania; the time limits for delivery and installation shall be 30.12.2022, 14:00 (2:00 PM) and the Incoterm applicable shall be [DDP]. The implementation period of tasks shall run from 30.09.2022. Specify the date on which implementation of the tasks is to commence to 30.12.2022.

1.2	The contractor shall comply strictly with the terms of the special conditions and the technical annex.

- Article 2	Origin

The rules of origin of the goods are defined in Article 10 of the special conditions.

When required, a certificate of origin for the goods must be provided by the contractor at the latest when it requests provisional acceptance of the goods. Failure to comply with this condition may result in the termination of the contract and/or suspension of payment.

- Article 3	Price

3.1	The price of the supplies shall be that shown on the financial offer (specimen in Annex IV). The total maximum contract price shall be LEK only for indirect management in the following cases: (i) when legal or local constraints exceptionally impose using the national currency; (ii) when needed, for contracts within the impress component of a programme estimate].<insert price>

3.2 	Payments shall be made in accordance with the general and/or special conditions (Articles 26 to 28).

- Article 4	Order of precedence of contract documents

The contract is made up of the following documents, in order of precedence:

- the contract agreement;

- the special conditions

- the general conditions (Annex I);

- the technical specifications (Annex II [including clarifications before the deadline for submission of tenders and minutes from the information meeting/site visit];

- the technical offer (Annex III [including clarifications from the tenderer provided during tender evaluation]);

- the budget breakdown (Annex IV);

specified forms and other relevant documents (Annex V)];

- The various documents making up the contract shall be deemed to be mutually explanatory; in cases of ambiguity or divergence, they shall prevail in the order in which they appear above.

- Article 5	Other specific conditions applying to the contract

For the purpose of Article 44 of the general conditions, for the part of the data transferred by the contracting authority to the European Commission:

(b) the data protection notice is available at http://ec.europa.eu/europeaid/prag/annexes.do?chapterTitleCode=A.

Done in English in three originals, For indirect management: one original being for the contracting authority, one original being for the European Commission, and one original being for the contractor.

| For the contractor |  | For the contracting authority |  |
| --- | --- | --- | --- |
| Name: |  | Name: |  |
| Title: |  | Title: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

- SPECIAL CONDITIONS

- CONTENTS

These conditions amplify and supplement, if necessary, the general conditions governing the contract. Unless the special conditions provide otherwise, those general conditions remain fully applicable. The numbering of the articles of the special conditions is not consecutive but follows the numbering of the articles of the general conditions. In exceptional cases, and with the authorisation of the appropriate Commission departments, other clauses may be added to cover specific situations.

Article 2	Language of the contract

2.1	The language used shall be English.

Article 4	Communications

4.1	The expert shall communicate with the Contracting Authority through info@qarkuvlore.gov.al and/or through institutional communication based on the internal rules for the documentation.

4.2	An electronic system will be used by the contracting authority and the contractor for all stages of implementation including, inter alia, management of the contract (amendments and administrative orders), reporting (including reporting on results) and payments.  The contractor will be required to register in and use the appropriate electronic exchange system to allow for the e-management of the contract.

The electronic management of the contract through the aforementioned system may commence on the date on which implementation of the contract starts, as described in Article 18 below, or at a later date. In the latter case, the contracting authority will inform the contractor in writing that he will be required to use the electronic system for all communications within a maximum period of 3 months.

Article 6	Subcontracting

N/A

6.3	EDF only: When selecting subcontractors, the contractor must give preference to natural persons or companies from ACP States capable of implementing the tasks required on similar terms.

Article 7	Supply of documents

Before the contractor places the order for the Equipment, he must bring to the CA the catalogs and manuals from the manufacturer for the approval of the Order. This will be notified in writing by the CA and the Consultant or Project Supervisor with the conclusion of the contract.

Article 8	Assistance with local regulations

In order to fulfil the obligations of this contract the contractor will be assisted from the project supervisor, the hydro-engineer, who will give all the necessary information of the local regulations.

Article 9	General obligations

9.9	The Project Beneficiaries must mark the objects financed from the Programme funds with a sticker, information sign, billboard or board of gratitude with the Logo, or place the Logo on the object during production, according to the nature of the object and the conditions prescribed in this guide. Larger objects (equipment etc.) with a sticker of approximately 120×50 mm. All these actions are in order to comply with its minimum obligation toward visibility. For more details please follow the information in the Communication and Visibility Manual for EU External Actions published on the  website of DG International Partnerships: https://ec.europa.eu/europeaid/funding/communication-and-visibility-manual-eu-external-actions_en .

Article 10	Origin

- 10.1	Under the Multiannual Financial Framework 2014-2020 (contracts/lots above EUR 100 000 under CIR and irrespective of the value for other instruments): All goods purchased must originate in an eligible source country as defined in the relevant instrument financing the project/programme Greece-Albania 2014-2020. For these purposes, ‘origin’ means the place where the goods are mined, grown, produced or manufactured. The origin of the goods must be determined according to the EU Customs Code or to the relevant international agreement applicable.

Article 11	Performance guarantee

11.1	No performance guarantee is required.

Article 12	Liabilities and insurance

12.1(a)	By way of derogation from Article 12.1(a), paragraph 2, of the general conditions, compensation for damage to the supplies resulting from the contractor's liability in respect of the contracting authority is capped at an amount equal to double price of the damaged supplies.

12.1 By way of derogation from Article 12.1(b), paragraph 2, of the general conditions, compensation for damage resulting from the contractor's liability in respect of the contracting authority is capped at an amount equal to the value of this contract.

12.2(a), paragraph 1	The supplies must be equipped with:

a) Manufacturer's or supplier's certificate

b) Pump manual

c) Manufacturer's or supplier's warranty of not less than 1 year

Specific requirements on when the requirements of proof of completion of adequate insurance must be provided:

See Article 12.2(a), paragraph 1, of the general conditions.

12.2(a), paragraph 2	Specific requirements on when the requirements of communication of cover notes and/or insurance certificates must be fulfilled:

See Article 12.2(a), paragraph 2, of the general conditions

12.2(b), paragraph 2	It is foreseen for the contractor will use its own means of transport to carry the goods to the Contracting Authority at the delivery destination in Vlora city, Albania and the local transport for the delivery and installation of the equipment at the relevant sites.

This type of insurance will vary depending on the nature of transport (land, air or sea) and the nature of the risks to be covered: loading, intermediate storage, unloading, including stowage and protection, theft, damage, loss, wetting, etc.

In the case of use of Incoterms, the contractor shall provide transport insurance to the extent that it assumes transportation risks. The question of the extent of the risks assumed by the contractor (seller) depends in particular on the Incoterms used:

- DDP - Delivered Duty Paid: Incoterm which imposes on the seller maximum obligations vis-à-vis transportation and loss risks and damage associated with the goods:

‘the seller delivers the goods when the goods are placed at the disposal of the buyer, cleared for import on the arriving means of transport ready for unloading at the named place of destination. The seller bears all the costs and risks involved in bringing the goods to the place of destination and has an obligation to clear the goods not only for export but also for import, to pay any duty for both export and import and to carry out all customs formalities.’ The transfer of risks and costs occurs at the place of unloading of the goods at the agreed place of destination.

Article 13	Programme of implementation of tasks

13.2	For the Lot 1: 07.10.2022 the signature of the contract; up to 17.10.2022 the delivery of the catalogue; up to 19.12. 2022 the delivery of the supplies in Vlora, up to 30.12. 2022 the installation and the test of the supplies;

Article 14	Contractor’s drawings

14.1	The contractor must bring the Catalog of the pump that he proposes to supply from eligible countries and deposit the Catalog to the Contract Supervisor.

Article 15	Sufficiency of tender prices N/A

15.1	 Article 15 of the general conditions

Article 16	Tax and customs arrangements

16.1	N/A Specify if the delivery conditions are DAP instead of DDP as mentioned in the general conditions

Article 17	Patents and licences

17.1	Article 17 of the general conditions

Article 18	Commencement order

18.1	07.10.2022

Article 19	Period of implementation of the tasks

19.1	07.10.2022 – 30.12.2022

Article 24	Quality of supplies

24.2	The contractor must bring the Catalog of the pump that he proposes to supply from eligible countries and deposit the Catalog to the Contract Supervisor.

Article 25	 Inspection and testing

25.2	The Contractor will be assisted form the project supervisor, the hydro engineer expert during all the stages of inspection and testing, alongside with the project manager.

Article 26	General principles for payments

26.1	Payments shall be made in LEK.

Pre-financing is not applicable to this contract

Payments shall be authorised and made by The Sector of Finance /Budget and Services of the Contracting Authority.

26.3	Contract in indirect management under the general budget of the Union only: By derogation, the final payment to the contractor of the amounts due shall be made within 90 days after receipt by the contracting authority of an invoice and of the application for the certificate of provisional acceptance.

26.5	In order to obtain payments, the contractor must forward to the authority referred to in paragraph 26.1 above:

b)	For the 60 % balance, the invoice(s) in triplicate together with the request for provisional acceptance of the supplies.

26.9	N/A Specify whether the contract includes a price revision clause. This clause must be drawn up by the competent services of the European Commission in accordance with their internal procedures.

Article 28	Delayed payments

28.2	For indirect management:

By derogation from Article 28.2 of the general conditions, once the deadline laid down in Article 26.3 has expired, the contractor shall, upon demand, be entitled to late-payment interest at the rate and for the period mentioned in the general conditions. The demand must be submitted within two months of receiving late payment.

Article 29	Delivery

29.3 Supplies that will be delivered and installed from the contractor must be equipped with:

a) Certificate of manufacturer or supplier

b) Pump manual

c) Manufacturer or supplier warranty not less than 1 year

The packaging shall remain the property of the contractor subject to environmental considerations.

29.5/6/7

Also, Equipment such as Inverter, Sensors, Electro Valves, blower, chlorination pump must be equipped with the following documents:

a) Certificate of manufacturer or supplier

b) Pump manual

c) Manufacturer or supplier warranty not less than 1 year

Article 31	Provisional acceptance

The certificate of provisional acceptance must be issued using the template in Annex C11.

Article 32	Warranty obligations

32.6	N/A Specify any additional obligations under the warranty, e.g. commercial warranty.

32.7	N/A The warranty must remain valid for one year after provisional acceptance.

Article 33	After-sales service N/A

33.1	Give details of any after-sales service that the contractor must provide and specify the proportion of the performance guarantee assigned to that activity.

Article 40	Settlement of disputes

40.4	Any disputes arising out of or relating to this contract which cannot be settled otherwise shall be referred to the exclusive jurisdiction of Vlora Judicial District Court in accordance with the national legislation of the state of the contracting authority.

Article 44	Data protection

[1. Processing of personal data related to the implementation of the contract by the contracting authority takes place in accordance with the national legislation of the state of the contracting authority and with the provisions of the respective financing agreement.

2. To the extent that the contract covers an action financed by the European Union, the Contracting Authority may share communications related to the implementation of the contract, with the European Commission. These exchanges shall be made to the Commission, solely for the purpose of allowing the latter to exercise its rights and obligations under the applicable legislative framework and under the financing agreement with the Partner country – contracting authority. The exchanges may involve transfers of personal data (such as names, contact details, signatures and CVs) of natural persons involved in the implementation of the contract (such as contractors, personnel, experts, trainees, subcontractors, insurers, guarantors, auditors and legal counsel). In cases where the contractor is processing personal data in the context of the implementation of the contract, he/she shall accordingly inform the data subjects of the possible transmission of their data to the Commission. When personal data is transmitted to the Commission, the latter processes them in accordance with Regulation (EU) 2018/1725 of the European Parliament and of the Council of 23 October 2018 on the protection of natural persons with regard to the processing of personal data by the Union institutions, bodies, offices and agencies and on the free movement of such data, and repealing Regulation (EC) No 45/2001 and Decision No 1247/2002/EC and as detailed in the specific privacy statement published at ePRAG.]

Article 45	Further additional clauses N/A

- DRAFT CONTRACT

SUPPLY CONTRACT FOR EUROPEAN

UNION EXTERNAL ACTIONS

No PILOT 04/SAVE WATER / Lot 2

financed from General budget of the Union

in the frame work of Interreg IPA II cross-border cooperation programme Greece - Albania 2014-2020

Keshilli i Qarkut Vlore, Pallati i Kultures “Laberia”, kati 3, Vlore, aLBANIA

(‘The contracting authority’),

of the one part,

and

<Full official name of contractor>

[<Legal status/title>]

[<Official registration number>]

<Full official address>

[<VAT number>], (‘the contractor’)

of the other part,

have agreed as follows:

- PROJECT Improving water management and supply infrastructure via smart technologies, policies and tools SAVE-WATER

- CONTRACT TITLE Sensors for the monitoring of Water Supply System (supply and installation)  / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

- Identification number < PILOT 04/SAVE WATER >

- Article 1	Subject

  - The subject of the contract shall be:

the supply, delivery, unloading, siting and installation, commissioning,

of the following supplies of lot no 2:

SENSORS

- 4G/3G AP EU	Meshlium is an IoT gateway that may contain up to 4 different radio interfaces: a WiFi 2.4 GHz (Access Point), a 4G/3G/GPRS/GSM and 2 XBee/RF radios. Meshlium may include Bluetooth, BLE and Wi-Fi radios too for scanning applications.  allow Meshlium to be placed outdoors.  (SUPPLY + SETTING)

- Plugging Sensor base: To ensure the placement of sensor probes. 2-to provide reading of parameters required by sensors.3-to have internal memory SD card.4-to connect to devices with protocol can use Lora Wan, sigfox, 4G, WiFi.5-To ensure data transmission in different formats to data center, as well as be able to connect to the cloud.6-provide replacement and changeable of sensors. To be remoter monitor (SUPPLY + SETTING)

- Conductivity Probe	Sensor connection probes (SUPPLY + SETTING)

- Horizontal liquid level (water)	Sensor + probe (SUPPLY + SETTING)

- Water flow medium	Sensor + probe (SUPPLY + SETTING)

- Ammonium Ion (NH4	Calibration Kit (SUPPLY + SETTING)

- Multi-Ions Calibration Kit (Ammonium, Calcium,	Sensor + probe (SUPPLY + SETTING)

- Chloride, Magnesium, Nitrate, Potassium, Sodium)

- Nitrate Ion 	Sensor + probe (SUPPLY + SETTING)

- Cupric Ion (Cu2+)	Sensor + probe (SUPPLY + SETTING)

- Soil moisture sensor	Sensor + probe (SUPPLY + SETTING)

- Oxidation Reduction Potential Sensor	Sensor + probe (SUPPLY + SETTING)

- Dissolved Oxygen Maintenance Kit	Maintenance Kit (SUPPLY + SETTING)

- Dissolved Oxygen sensor	Sensor + probe (SUPPLY + SETTING)

- Soil/Water temperature Probe	Sensor + probe (SUPPLY + SETTING)

- External solar panel 7V - 500mA 	External solar power supply (SUPPLY + SETTING)

- outdoors USB cable	2m (SUPPLY + SETTING)

- USB-220 V Adapter	 (SUPPLY + SETTING)

- International adapter	 (SUPPLY + SETTING)

- Conductivity Calibration Kit	 (SUPPLY + SETTING)

- pH Calibration Kit	 (SUPPLY + SETTING)

- DO Calibration Solution	 (SUPPLY + SETTING)

- ORP Calibration Solution 	 (SUPPLY + SETTING)

- Internet connection 4 point 12 months	 (SUPPLY + SETTING)

- DO Calibration Solution	 (SUPPLY + SETTING)

- ORP Calibration Solution 	 (SUPPLY + SETTING)

- Turbidity calibration solution, 	 (SUPPLY + SETTING)

- Storage solution for PHEHT probe 	 (SUPPLY + SETTING)

- Sensor protection accessory 	 (SUPPLY + SETTING)

- Prob cable Extensions 1m,1.5m 	 (SUPPLY + SETTING)

- Registration on cloud services 5 users	 (SUPPLY + SETTING)

- Laptop core i7, gen ≥10, SSD 500 GB, 15.6” monitor, MEMORY RAM 16GB, 6 USB ports, power supply eu,lan.WIFI, blutooth

The place of acceptance of the supplies shall be in Vlore, at pilot site (Babice e Madhe) , the time limits for delivery and installation shall be 30.12.2022, 14:00 (2 PM) and the Incoterm applicable shall be [DDP]. The implementation period of tasks shall run from 30.09.2022. The tasks is to commence to 30.09.2022.

1.2	The contractor shall comply strictly with the terms of the special conditions and the technical annex.

- Article 2	Origin

The rules of origin of the goods are defined in Article 10 of the special conditions.

When required, a certificate of origin for the goods must be provided by the contractor at the latest when it requests provisional acceptance of the goods. Failure to comply with this condition may result in the termination of the contract and/or suspension of payment.

- Article 3	Price

3.1	The price of the supplies shall be that shown on the financial offer (specimen in Annex IV). The total maximum contract price shall be LEK only for indirect management in the following cases: (i) when legal or local constraints exceptionally impose using the national currency; (ii) when needed, for contracts within the impress component of a programme estimate].<insert price>

3.2 	Payments shall be made in accordance with the general and/or special conditions (Articles 26 to 28).

- Article 4	Order of precedence of contract documents

The contract is made up of the following documents, in order of precedence:

- the contract agreement;

- the special conditions

- the general conditions (Annex I);

- the technical specifications (Annex II [including clarifications before the deadline for submission of tenders and minutes from the information meeting/site visit];

- the technical offer (Annex III [including clarifications from the tenderer provided during tender evaluation]);

- the budget breakdown (Annex IV);

- [specified forms and other relevant documents (Annex V)];

- The various documents making up the contract shall be deemed to be mutually explanatory; in cases of ambiguity or divergence, they shall prevail in the order in which they appear above.

- Article 5	Other specific conditions applying to the contract

[For the purpose of Article 44 of the general conditions, for the part of the data transferred by the contracting authority to the European Commission:

(a) the controller for the processing of personal data carried out within the Commission is

[For DG INTPA the head of legal affairs unit of DG International Partnerships.]

[For DG NEAR the head of contracts and finance unit R4 of DG Neighbourhood and Enlargement Negotiations][For any other DG <please add the function of your controller >.]

(b) the data protection notice is available at http://ec.europa.eu/europeaid/prag/annexes.do?chapterTitleCode=A.

Done in English in [three] originals: one original being for the contracting authority, one original being for the European Commission, and one original being for the contractor.

| For the contractor |  | For the contracting authority |  |
| --- | --- | --- | --- |
| Name: |  | Name: |  |
| Title: |  | Title: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

- SPECIAL CONDITIONS

- CONTENTS

These conditions amplify and supplement, if necessary, the general conditions governing the contract. Unless the special conditions provide otherwise, those general conditions remain fully applicable. The numbering of the articles of the special conditions is not consecutive but follows the numbering of the articles of the general conditions. In exceptional cases, and with the authorisation of the appropriate Commission departments, other clauses may be added to cover specific situations.

Article 2	Language of the contract

2.1	The language used shall be English.

Article 4	Communications

4.1 The expert shall communicate with the Contracting Authority through info@qarkuvlore.gov.al and/or through institutional communication based on the internal rules for the documentation.

4.2	An electronic system will be used by the contracting authority and the contractor for all stages of implementation including, inter alia, management of the contract (amendments and administrative orders), reporting (including reporting on results) and payments.  The contractor will be required to register in and use the appropriate electronic exchange system to allow for the e-management of the contract.

The electronic management of the contract through the aforementioned system may commence on the date on which implementation of the contract starts, as described in Article 18 below, or at a later date. In the latter case, the contracting authority will inform the contractor in writing that he will be required to use the electronic system for all communications within a maximum period of 3 months.

Article 6	Subcontracting

N/A

6.3	EDF only: When selecting subcontractors, the contractor must give preference to natural persons or companies from ACP States capable of implementing the tasks required on similar terms.

Article 7	Supply of documents N/A

Indicate here the documents, drawings to be supplied and, if necessary, the procedure to be used by the contracting authority and the project manager to approve drawings and other documents provided by the contractor

Article 8	Assistance with local regulations N/A

Specify the procedures for obtaining permits, visas, authorisation or licences or, at least, specify the relevant reference texts, if necessary

Article 9	General obligations

9.9	The Project Beneficiaries must mark the objects financed from the Programme funds with a sticker, information sign, billboard or board of gratitude with the Logo, or place the Logo on the object during production, according to the nature of the object and the conditions prescribed in this guide. All these actions are in order to comply with its minimum obligation toward visibility. For more details please follow the information in the Communication and Visibility Manual for EU External Actions published on the  website of DG International Partnerships: https://ec.europa.eu/europeaid/funding/communication-and-visibility-manual-eu-external-actions_en .

Article 10	Origin

- 10.1	All goods purchased can originate in any country.

Article 11	Performance guarantee

11.1	No performance guarantee is required.

Article 12	Liabilities and insurance

12.1(a)	By way of derogation from Article 12.1(a), paragraph 2, of the general conditions, compensation for damage to the supplies resulting from the contractor's liability in respect of the contracting authority is capped at an amount equal to double price of the damaged supplies.

12.1 By way of derogation from Article 12.1(b), paragraph 2, of the general conditions, compensation for damage resulting from the contractor's liability in respect of the contracting authority is capped at an amount equal to the value of this contract.

12.2(a), paragraph 1	Article 12.2(a), paragraph 1, of the general conditions

12.2(a), paragraph 2	Article 12.2(a), paragraph 2, of the general conditions

12.2(b), paragraph 2	It is foreseen for the contractor will use its own means of transport to carry the goods to the Contracting Authority at the delivery destination in Vlora city, Albania and the local transport for the delivery and installation of the equipment at the relevant site.

This type of insurance will vary depending on the nature of transport (land, air or sea) and the nature of the risks to be covered: loading, intermediate storage, unloading, including stowage and protection, theft, damage, loss, wetting, etc.

In the case of use of Incoterms, the contractor shall provide transport insurance to the extent that it assumes transportation risks. The question of the extent of the risks assumed by the contractor (seller) depends in particular on the Incoterms used:

- DDP - Delivered Duty Paid: Incoterm which imposes on the seller maximum obligations vis-à-vis transportation and loss risks and damage associated with the goods:

‘the seller delivers the goods when the goods are placed at the disposal of the buyer, cleared for import on the arriving means of transport ready for unloading at the named place of destination. The seller bears all the costs and risks involved in bringing the goods to the place of destination and has an obligation to clear the goods not only for export but also for import, to pay any duty for both export and import and to carry out all customs formalities.’ The transfer of risks and costs occurs at the place of unloading of the goods at the agreed place of destination.

Article 13	Programme of implementation of tasks

13.2	For the Lot 2:

10.10.2022 the signature of the contract;

up to 25.11. 2022 the delivery of the supplies in Vlora,

up to 15.12. 2022 the installation and the test of the supplies;

Article 14	Contractor’s drawings N/A

14.1	Specify the drawings and/or samples required from the contractor, the procedures for approving them and any requirements relating to manuals.

Article 15	Sufficiency of tender prices

15.1	See Article 15 of the general conditions

Article 16	Tax and customs arrangements

16.1	N/A Specify if the delivery conditions are DAP instead of DDP as mentioned in the general conditions

Article 17	Patents and licences

17.1	Article 17 of the general conditions

Article 18	Commencement order

18.1	10.10.2022

Article 19	Period of implementation of the tasks

19.1	10.10.2022 – 15.12.2022

Article 24	Quality of supplies N/A

24.2	Indicate here if a preliminary technical acceptance is required

Article 25	Inspection and testing

25.2	The Contractor will be assisted form the project supervisor, the electronic engineer expert during all the stages of inspection and testing, alongside with the project manager.

Article 26	General principles for payments

26.1	Payments shall be made in LEK.

Pre-financing is not applicable to this contract

Payments shall be authorised and made by The Sector of Finance /Budget and Services of the Contracting Authority.

26.3	Contract in indirect management under the general budget of the Union only: By derogation, the final payment to the contractor of the amounts due shall be made within 90 days after receipt by the contracting authority of an invoice and of the application for the certificate of provisional acceptance.

26.5	In order to obtain payments, the contractor must forward to the authority referred to in paragraph 26.1 above:

b)	For the 60 % balance, the invoice(s) in triplicate together with the request for provisional acceptance of the supplies.

26.9	N/A Specify whether the contract includes a price revision clause. This clause must be drawn up by the competent services of the European Commission in accordance with their internal procedures.

Article 28	Delayed payments

28.2	For indirect management:

By derogation from Article 28.2 of the general conditions, once the deadline laid down in Article 26.3 has expired, the contractor shall, upon demand, be entitled to late-payment interest at the rate and for the period mentioned in the general conditions. The demand must be submitted within two months of receiving late payment.

Article 29	Delivery

29.3	The packaging shall remain the property of the contractor subject to environmental considerations.

Article 31	 Provisional acceptance

The certificate of provisional acceptance must be issued using the template in Annex C11.

Article 32	 Warranty obligations

32.6	N/A Specify any additional obligations under the warranty, e.g. commercial warranty.

32.7	N/A The warranty must remain valid for one year after provisional acceptance.

Article 33	After-sales service N/A

33.1	Give details of any after-sales service that the contractor must provide and specify the proportion of the performance guarantee assigned to that activity.

Article 40	Settlement of disputes

40.4	Any disputes arising out of or relating to this contract which cannot be settled otherwise shall be referred to the exclusive jurisdiction of <specify> in accordance with the national legislation of the state of the contracting authority.

Article 44	Data protection

[1. Processing of personal data related to the implementation of the contract by the contracting authority takes place in accordance with the national legislation of the state of the contracting authority and with the provisions of the respective financing agreement.

2. To the extent that the contract covers an action financed by the European Union, the Contracting Authority may share communications related to the implementation of the contract, with the European Commission. These exchanges shall be made to the Commission, solely for the purpose of allowing the latter to exercise its rights and obligations under the applicable legislative framework and under the financing agreement with the Partner country – contracting authority. The exchanges may involve transfers of personal data (such as names, contact details, signatures and CVs) of natural persons involved in the implementation of the contract (such as contractors, personnel, experts, trainees, subcontractors, insurers, guarantors, auditors and legal counsel). In cases where the contractor is processing personal data in the context of the implementation of the contract, he/she shall accordingly inform the data subjects of the possible transmission of their data to the Commission. When personal data is transmitted to the Commission, the latter processes them in accordance with Regulation (EU) 2018/1725 of the European Parliament and of the Council of 23 October 2018 on the protection of natural persons with regard to the processing of personal data by the Union institutions, bodies, offices and agencies and on the free movement of such data, and repealing Regulation (EC) No 45/2001 and Decision No 1247/2002/EC and as detailed in the specific privacy statement published at ePRAG.]

Article 45	Further additional clauses N/A

* * *

ANNEX I: GENERAL CONDITIONS
FOR SUPPLY CONTRACTS FINANCED BY THE EUROPEAN UNION OR BY THE
EUROPEAN DEVELOPMENT FUND

ATTACHED AS PDF

- ANNEX II + III:	 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER

- Contract title: Supply of < Water Supply Products for the Water Supply System (supply and installation) / LOT 1 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.>	p 1 /…

Publication reference: < PILOT 02/SAVE WATER >

Columns 1-2 should be completed by the contracting authority

Columns 3-4 should be completed by the tenderer

Column 5 is reserved for the evaluation committee

Annex III - the contractor's technical offer

The tenderers are requested to complete the template on the next pages:

- Column 2 is completed by the contracting authority shows the required specifications (not to be modified by the tenderer),

- Column 3 is to be filled in by the tenderer and must detail what is offered (for example the words ‘compliant’ or ‘yes’ are not sufficient)

- Column 4 allows the tenderer to make comments on its proposed supply and to make eventual references to the documentation

The eventual documentation supplied should clearly indicate (highlight, mark) the models offered and the options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the evaluation committee.

The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications.

| 1. Item number | 2. Specifications required | 3. Specifications offered | 4. Notes, remarks, ref to documentation | 5. Evaluation committee’s notes |
| --- | --- | --- | --- | --- |
| 1 item Submersible electric pump. | P= 37 kW; H= 210m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel; |  |  |  |
| 1 item Centrifugal electric pump. | P= 32 kW; H= 150m; Q= 15 l/s; Combined with the electric release panel; |  |  |  |
| 1 item Submersible electric pump. | P= 26 kW; H= 150m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel; |  |  |  |
| 1 item Centrifugal electric pump. | P= 132 kW; H= 370m; Q= 15 l/s; Combined with the electric release panel; Ω=1400 no.spins/min |  |  |  |
| 2 item Submersible electric pump | P= 22 kW; H= 120m; Q= 15 l/s; Diameter of electric motor pump Φ= 4"; Combined with the electric release panel; |  |  |  |
| 2 item Submersible electric pump. | P= 37 kW; H= 260m; Q= 12 l/s; Diameter of electric motor pump Φ= 6"; Combined with the electric release panel; |  |  |  |
| 2 item Chlorination dosing pumps. | Type DMH 252, PVC 45-16 AR 0.18KW 50Hz Ω=1340 no.spins/min PN= 16-20 bar |  |  |  |
| 2 item Centrifugal electric pump. | P= 7.5 kW; H= 45m; Q= 15 l/s; Combined with the electric release panel; |  |  |  |
| 1 item Centrifugal electric pump | P= 15 kW; H= 40m; Q= 30 l/s; Combined with the electric release panel; |  |  |  |
| 1 item Centrifugal electric pump. | P= 37 kW; H= 150m; Q= 15 l/s; Combined with the electric release panel; |  |  |  |
| 2 item Submersible electric pump. | P= 75 kW; H= 280m; Q= 12 l/s; Diameter of electric motor pump Φ= 8"; Combined with the electric release panel; |  |  |  |
| 2 item Vertical Centrifugal Electric Pump | . P= 30 kW; H= 160m; Q= 15 l/s; Combined with the electric release panel; |  |  |  |
| 1 item Inverter (Allen Brandley PowerFlex type or equivalent with it) | 700h series b, 250kW |  |  |  |
| 3 item Vacuum Pump (SIHI LEMA type or equivalent with it) 26 51. | P= 0.75 - 1.1 kW |  |  |  |
| 10 item Sensor, power outage and alarm (Vegaswing type or equivalent with it) 51. | SG51XXSGATPM 10-55 volt; transistor PNP; IP67 |  |  |  |
| 10 item Electric Valve (Danfoss type or equivalent with it) 1/4 " 24 VAC; | code EV210B, series 032U1220 |  |  |  |
| 10 item Inverter blower PowerFlex 700 h series b, | Ebompopapst R2E280-AE 52-17; 230V, 50Hz, 1.0A, 225W, 2700 spins/min; with condenser 7μF, 400VDC accompanied by cable and contact |  |  |  |
| 5 item Module HIM 20C-C3S, for Inverter (Allen Brandley PowerFlex type or equivalent with it) 700 h series b | The PowerFlex 700H AC drive offers low-cost, variable-speed applications. Ratings currently available include 200…1900 HP at 480V AC, 150…2400 HP at 600V AC, and 160…2000 kW at 690V AC input. An LCD human interface module (also used with the PowerFlex® 70, 700, and 700S) provides text for startup, measurement, programming, and troubleshooting. PowerFlex 700H AC drives are configurable for Volts-per-Hertz or Sensorless Vector control modes to meet a wide variety of application needs. This control is located in a module which can be removed separately from the power structure. The control module is the same for all drive ratings, simplifying installation and maintenance for the entire product line. Optional I/O is available as 24V DC or 115V AC. |  |  |  |
| 1 item Converter IFC 100, for water measurements (KROHNE type or equivalent with it) | The IFC 100 offers an accuracy of ±0.3% of the measured value, while providing extremely fast signal conversion and digital signal processing so that processes can be reliably controlled. A large, illuminated display and intuitive menu make it easy to set up and operate, even in difficult conditions. The IFC 100 provides current output, pulse/frequency output, status output and control input. A HART interface is included as standard. The IFC 100 is available in a variety of mounting configurations. A wall mount version allows for remote installations. The integral mounting unit is available in 0° or 45° versions for improved display readability. The 0° version is ideal for installation in vertical pipes while the 45° is for horizontal pipes. Both housing versions can be rotated by 90° elevation, allowing for customer-specific installation positions. |  |  |  |
| 4 item Wheeled mobile water pump with diesel engine | The Portable water pumps Portable water pumps provide a wide range of use for the transfer or delivery of pure/pure water or water-containing wastes. They can also provide vital backup in case of floods and overflow incidents. The pumps are ideal for use in pools and ponds or during disasters such as floods. It has a Diesel Generator with unmatched uptime. A single tank of diesel runs for 8 hours. The portable diesel pump consumes less than one liter per working hour. |  |  |  |
| 4 item Submersible electric pump with switch. | Exit Φ= 2"; P= 1.5 kW; H= 1-18m; Q= 1.7-15l/s |  |  |  |
| 4 item Diesel motor-generator | S= 6 kVA |  |  |  |

ANNEX II + III:	 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER

Contract title: Supply of Sensors for the monitoring of Water Supply System (supply and installation) / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.>	p 1 /…

Publication reference: < PILOT 02/SAVE WATER >

Columns 1-2 should be completed by the contracting authority

Columns 3-4 should be completed by the tenderer

Column 5 is reserved for the evaluation committee

Annex III - the contractor's technical offer

The tenderers are requested to complete the template on the next pages:

- Column 2 is completed by the contracting authority shows the required specifications (not to be modified by the tenderer),

- Column 3 is to be filled in by the tenderer and must detail what is offered (for example the words ‘compliant’ or ‘yes’ are not sufficient)

- Column 4 allows the tenderer to make comments on its proposed supply and to make eventual references to the documentation

The eventual documentation supplied should clearly indicate (highlight, mark) the models offered and the options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the evaluation committee.

The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications.

| 1. Item number | 2. Specifications required | 3. Specifications offered | 4. Notes, remarks, ref to documentation | 5. Evaluation committee’s notes |
| --- | --- | --- | --- | --- |
| 4G/3G AP EU | Meshlium is an IoT gateway that may contain up to 4 different radio interfaces: a WiFi 2.4 GHz (Access Point), a 4G/3G/GPRS/GSM and 2 XBee/RF radios. Meshlium may include Bluetooth, BLE and Wi-Fi radios too for scanning applications. allow Meshlium to be placed outdoors. (SUPPLY + SETTING) |  |  |  |
| Pluging Senssor base | 1-To ensure the placement of sensor probes. 2-to provide reading of parameters required by sensors.3-to have internal memory SD card.4-to connect to devices with protocol can use Lora Wan, sigfox, 4G, WiFi.5-To ensure data transmission in different formats to data center, as well as be able to connect to the cloud.6-provide replacement and changeable of sensors. To be remotor monitor (SUPPLY + SETTING) |  |  |  |
| Conductivity Probe | Sensor connection probes (SUPPLY + SETTING) |  |  |  |
| Horizontal liquid level (water) | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| Water flow medium | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| Ammonium Ion (NH4 | Calibration Kit (SUPPLY + SETTING) |  |  |  |
| Multi-Ions Calibration Kit (Ammonium, Calcium, Chloride, Magnesium, Nitrate, Potassium, Sodium) | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| Nitrate Ion | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| Cupric Ion (Cu2+) | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| Soil moisture sensor | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| Oxidation Reduction Potential sensor | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| Dissolved Oxygen Maintenance Kit | Maintenance Kit (SUPPLY + SETTING) |  |  |  |
| Dissolved Oxygen sensor | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| Soil/Water temperature Probe | Sensor + probe (SUPPLY + SETTING) |  |  |  |
| External solar panel 7V - 500mA | External solar power supply (SUPPLY + SETTING) |  |  |  |
| outdoors USB cable | 2m (SUPPLY + SETTING) |  |  |  |
| USB-220 V Adapter | (SUPPLY + SETTING) |  |  |  |
| International adapter | (SUPPLY + SETTING) |  |  |  |
| Conductivity Calibration Kit | (SUPPLY + SETTING) |  |  |  |
| pH Calibration Kit | (SUPPLY + SETTING) |  |  |  |
| DO Calibration Solution | (SUPPLY + SETTING) |  |  |  |
| ORP Calibration Solution | (SUPPLY + SETTING) |  |  |  |
| Internet connection 4 point 12 months | (SUPPLY + SETTING) |  |  |  |
| DO Calibration Solution | (SUPPLY + SETTING) |  |  |  |
| ORP Calibration Solution | (SUPPLY + SETTING) |  |  |  |
| Turbidity calibration solution, | (SUPPLY + SETTING) |  |  |  |
| Storage solution for PHEHT probe | (SUPPLY + SETTING) |  |  |  |
| Sensor protection accessory | (SUPPLY + SETTING) |  |  |  |
| Prob cable Extensions 1m,1.5m | (SUPPLY + SETTING) |  |  |  |
| Registration on cloud services 5 users | (SUPPLY + SETTING) |  |  |  |
| Laptop core i7, gen ≥10, SSD 500 GB, 15.6” monitor, MEMORY RAM 16GB, 6 USB ports, power supply eu,lan.WIFI,blutooth | Laptop core i7, gen ≥10, SSD 500 GB, 15.6” monitor, MEMORY RAM 16GB, 6 USB ports, power supply eu,lan.WIFI,blutooth |  |  |  |

ANNEX IV: Budget breakdown (Model financial offer) to be tailored to the specific project

Page No 1 [of…]

| A |  | C | D | E |
| --- | --- | --- | --- | --- |
| Item number | Quantity | specifications offered (incl brand/model) | Unit costs with delivery DDP <place of acceptance> [EUR] [<LEK> only for indirect management in the following cases: (i) when legal or local constraints exceptionally impose using the national currency; (ii) when needed, for contracts within the imprest component of a programme estimate] | total [EUR] [<LEK> only for indirect management in the following cases: (i) when legal or local constraints exceptionally impose using the national currency; (ii) when needed, for contracts within the imprest component of a programme estimate] |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
|  |  | [Training] | [Lump sum] |  |
|  |  | [Other services and any other costs not directly related to the intrinsic value of the products] | [Lump sum] |  |
|  |  |  | Total |  |
|  |  | [Spare parts with detailed annex including unit prices] [Consumables with detailed annex including unit prices] [Life cycle costs with detailed annex including unit prices] | [Total cost] [Total cost] [Total cost] |  |

PUBLICATION REFERENCE: <reference number>	NAME OF TENDERER: <name>

ADMINISTRATIVE COMPLIANCE GRID

To be tailored to the specific project.

| Contract title : | Water Supply Products for the Water Supply System (supply and installation) / LOT 1 and Sensors for the monitoring of Water Supply System (supply and installation) / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools. | Publication reference : | REF: PILOT 04 /SAVE WATER |
| --- | --- | --- | --- |

| Is tenderer (consortium) nationality eligible? (Y/N) | Is documentation complete? (Y/N) | Is language as required? (Y/N) | Is tender submission form complete? (Y/N) | Is tenderer's declaration signed (by all consortium members if a consortium)? (Yes/No/ Not Applicable) | Declaration(s) of honour included? (Yes/No) | Other administrative requirements of the tender dossier? (Yes/No/Not applicable) | Overall decision? (Accept / Reject) |
| --- | --- | --- | --- | --- | --- | --- | --- |

| Chairperson's name |  |
| --- | --- |
| Chairperson's signature |  |
| Date |  |

EVALUATION GRID

| Contract title : | Water Supply Products for the Water Supply System (supply and installation) / LOT 1 and Sensors for the monitoring of Water Supply System (supply and installation) / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools. | Publication reference : | REF: PILOT 04 /SAVE WATER |
| --- | --- | --- | --- |

| Tender No | Name of tenderer | Rules of origin respected? (additional guidance) (Y/N) | Economic & financial capacity? (OK/a/b/…) | Professional capacity? (OK/a/b/…) | Technical capacity? (OK/a/b/…) | Compliance with technical specifications? (OK/a/b/…) | Ancillary services as required? (OK/a/b/…/NA) | Subcontracting statement in accordance with art. 6 of the general conditions? (Y/N) | Other technical requirements in tender dossier? (Yes/No/Not applicable) | Technically compliant? Y/N) | Justification/ notes: |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |

| Evaluator's name & signature |  |
| --- | --- |
| Evaluator's name & signature |  |
| Evaluator's name & signature |  |
| Date |  |

- TENDER FORM FOR A SUPPLY CONTRACT

Publication reference: < REF: PILOT 04 /SAVE WATER >

- Title of contract: < Water Supply Products for the Water Supply System / LOT 1 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools

- Or

- Title of contract: Sensors for the monitoring of Water Supply System / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools>

<Place and date>

A: <Name and address of contracting authority >.

[How to complete this tender submission form

Tenders submitted by consortia (i.e. either a permanent, legally-established grouping or a grouping constituted informally for a specific tender procedure) must follow the instructions applicable to the consortium leader and its members. In case of consortia, the tenderer’s declaration should be submitted by the leader and by all members of the consortium.

In case the instructions to tenderers (see section 10) state that the tender should be submitted by post or courier or hand delivered (paper submission): the attachments to this submission form (i.e. declarations, statements, proofs) may be in original or copy. The only exception is the Declaration on Honour on exclusion and selection criteria for which signed originals shall be submitted. For economical and ecological reasons, it is recommend that paper files are used and that plastic folders or dividers are avoided. It is also recommended to use double-sided printing as much as possible.

In case the instructions to tenderers (see section 10) state that the tender should be submitted via eSubmission: declarations and statements shall be signed, scanned and uploaded in eSubmission. The only exception is the Declaration on Honour on exclusion and selection criteria for which, in addition to scanned copies, signed originals shall be submitted. See further instructions below. Originals documents that have not been submitted must be kept by the tenderer. If requested, these originals documents must be dispatched to the contracting authority.

Delete this section highlighted in yellow after having completed all instructions.]

One signed form must be supplied (for each lot, if the tender procedure is divided into lots), together with the number of copies specified in the instructions to tenderers. The form must include a signed declaration using the annexed format from each legal entity submitting this tender. Any additional documentation (brochure, letter, etc.) sent with the form will not be taken into consideration. Tenders being submitted by a consortium (i.e. either a permanent, legally-established grouping or a grouping which has been constituted informally for a specific tender procedure) must follow the instructions applicable to the consortium leader and its members. The attachments to this submission form (i.e. declarations, statements, proofs) may be in original or copy. If copies are submitted, the originals must be dispatched to the contracting authority upon request. For economical and ecological reasons, we strongly recommend that you submit your files on paper-based materials (no plastic folder or divider). We also suggest you use double-sided print-outs as much as possible.

Capacity-providing entities

An economic operator (i.e. tenderer) may, where appropriate and for a particular contract, rely on the capacities of other entities, regardless of the legal nature of the links which it has with them. If the economic operator relies on other entities it must in that case prove to the contracting authority that it will have at its disposal the resources necessary for the performance of the contract by producing with the tender documents a commitment by those entities to place those resources at its disposal. Such entities, for instance the parent company of the economic operator, must respect the same rules of eligibility and notably that of nationality as the economic operator relying on them and must comply with the selection criteria for which the economic operator relies on them. For the purpose of the present tender, the data for this third entity for the relevant selection criterion has to be included in a separate document. Proof of the capacity will also have to be provided when requested by the contracting authority.

With regard to technical and professional criteria, an economic operator may only rely on the capacities of other entities where the latter will perform the tasks for which these capacities are required.

With regard to economic and financial criteria, the entities upon whose capacity the economic operator relies, become jointly and severally liable for the performance of the contract.

- 1	SUBMITTED BY

|  | Name(s) of tenderer(s) | Nationality |
| --- | --- | --- |
| Leader |  |  |
| Member |  |  |
| Etc … |  |  |

- 2	CONTACT PERSON (for this tender)

| Name |  |
| --- | --- |
| Address |  |
| Telephone |  |
| Fax |  |
| E-mail |  |

3	ECONOMIC AND FINANCIAL CAPACITY

Please complete the following table of financial data based on your annual accounts and your latest projections. If annual closed accounts are not yet available for the current year or past year, please provide your latest estimates in the columns marked with **. Figures in all columns must be calculated on the same basis to allow a direct, year-on-year comparison to be made (or, if the basis has changed, an explanation of the change must be provided as a footnote to the table). Any clarification or explanation which is judged necessary may also be provided.

| Financial data Data requested in this table must be consistent with the selection criteria set in the additional information about the contract notice document | 2 years before last year <specify> € | Year before last year <specify> € | Last year <specify> € | Average € | [Past year € ]** | [Current year €]** |
| --- | --- | --- | --- | --- | --- | --- |
| Annual turnover, excluding this contract |  |  |  |  |  |  |
| Current assets |  |  |  |  |  |  |
| Current liabilities |  |  |  |  |  |  |
| [Current ratio (current assets/current liabilities) | Not applicable | Not applicable |  | Not applicable | Not applicable | Not applicable] |

Please provide the following personnel statistics for the current year and the two previous years.

| Annual manpower | Year before past year |  | Past year |  | Current year |  | Period average |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Overall | Relevant fields | Overall | Relevant fields 11 | Overall | Relevant fields11 | Overall | Relevant fields11 |
| Permanent personnel |  |  |  |  |  |  |  |  |
| Other personnel |  |  |  |  |  |  |  |  |
| Total |  |  |  |  |  |  |  |  |
| Permanent personnel as a proportion of total personnel (%) | % | % | % | % | % | % | % % |  |

5	FIELDS OF SPECIALISATION

Please use the table below to indicate the specialisms relevant to this contract of each legal entity making this tender, by using the names of these specialisms as the row headings and the name of the legal entity as the column headings. Show the relevant specialism(s) of each legal entity by placing a tick () in the box corresponding to those specialisms in which the legal entity has significant experience. [Maximum 10 specialisms]

|  | Leader | Member 2 | Member 3 | Etc … |
| --- | --- | --- | --- | --- |
| Relevant specialism 1 |  |  |  |  |
| Relevant specialism 2 |  |  |  |  |
| Etc … |  |  |  |  |

6	EXPERIENCE

Please complete a table using the format below to summarise the major relevant supplies carried out over the past 3 years by the legal entity or entities making this tender. The number of references to be provided must not exceed 15 for the entire tender

| Ref # (maximum 15) | Project title |  | … |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Name of legal entity | Country | Overall supply value (EUR) | Proportion supplied by legal entity (%) | No of personnel provided | Name of client | Origin of funding | Dates | Name of members if any |
| … | … | … | … | … | … | … | … | … |
| Detailed description of supply |  |  |  |  |  | Related services provided |  |  |
| … |  |  |  |  |  | … |  |  |

- 7	TENDERER’S DECLARATION(S)

As part of their tender, each legal entity identified under point 1 of this form, including every consortium member, as well as each capacity-providing entity and each subcontractor, must submit a signed declaration using this format, together with the declaration on honour on exclusion and selection criteria (Annex 1) (insert Form a.14a).

In response to your letter of invitation to tender for the above contract,

we, the undersigned, hereby declare that:

1	We have examined and accept in full the content of the dossier for invitation to tender No <……………………………….> of <date>. We hereby accept its provisions in their entirety, without reservation or restriction.

2	[If the contract is financed by a basic act under the multiannual financial framework for the years 2014-2020] We offer to deliver, in accordance with the terms of the tender dossier and the conditions and time limits laid down, without reserve or restriction:

Lot 1: <description of supplies with indication of quantities and origin>

Lot 2: <description of supplies with indication of quantities and origin>

[If the contract is financed by a basic act under the multiannual financial framework for the years 2021-2027] We offer to deliver, in accordance with the terms of the tender dossier and the conditions and time limits laid down, without reserve or restriction:

Lot 1: <description of supplies with indication of quantities>

Lot 2: <description of supplies with indication of quantities>

3	The price of our tender excluding spare parts and consumables, if applicable (excluding the discounts described under point 4) is:

Lot 1: <insert price>

Lot 2: <insert price and currency>

Lot 3: <insert price>

4	We will grant a discount of [<…>%], or [<…………..>] [in the event of our being awarded lot … and lot … ………].

5	This tender is valid for a period of 90 days from the final date for submission of tenders.

6 	If our tender is accepted, we undertake to provide a performance guarantee as required by Article 11 of the special conditions.

7	Our firm/company [and our subcontractors] has/have the following nationality:

<……………………………………………………………………>

8	We are making this tender in our own right [as member in the consortium led by [< name of the leader >] [ourselves]*. We confirm that we are not tendering for the same contract in any other form. [We confirm, as a member in the consortium, that all members are jointly and severally liable by law for the execution of the contract, that the lead member is authorised to bind, and receive instructions for and on behalf of, each member, that the execution of the contract, including payments, is the responsibility of the lead member, and that all members in the joint venture/consortium are bound to remain in the joint venture/consortium for the entire period of the contract’s execution]. [We confirm, as capacity-providing entity to be jointly and severally bound in respect of the obligations under the contract, including for any recoverable amount.]

9	We undertake, if required, to provide the proof usual under the law of the country in which we are effectively established that we do not fall into any of the exclusion situations. The date on the evidence or documents provided will be no earlier than 1 year before the date of submission of the tender and, in addition, we will provide a statement that our situation has not altered in the period which has elapsed since the evidence in question was drawn up.

We also undertake, if required, to provide evidence of financial and economic standing and technical and professional capacity according to the selection criteria for this call for tender specified in the additional information about the contract notice. The documentary proofs required are listed in Section 2.6.11. of the practical guide.

10	We agree to abide by the ethics clauses in Clause 24 of the instructions to tenderers and, in particular, have no conflict of interests or any equivalent relation which may distort competition with other tenderers or other parties in the tender procedure at the time of the submission of this form.

We confirm that we, including all consortium members, if any, and subcontractors  are not in the lists of EU restrictive measures (www.sanctionsmap.eu)  and we understand that our tender may be rejected, if proved the contrary.

11	We will inform the contracting authority immediately if there is any change in the above circumstances at any stage during the implementation of the tasks. We also fully recognise and accept that any inaccurate or incomplete information deliberately provided in this tender may result in our exclusion from this and other contracts funded by the EU/EDF.

12 	We note that the contracting authority is not bound to proceed with this invitation to tender and that it reserves the right to award only part of the contract. It will incur no liability towards us should it do so.

13	We fully recognise and accept that if the above-mentioned persons participate in spite of being in any of the situations listed in Section 2.6.10.1.1. of the practical guide or if  the declarations or information provided prove to be false, they may be subject to rejection from this procedure and to administrative sanctions in the form of exclusion and financial penalties up to 10 % of the total estimated value of the contract being awarded and that this information may be published on the Commission website in accordance with the Financial Regulation in force.

14	We are aware that, for the purposes of safeguarding the EU's financial interests, our personal data may be transferred to internal audit services, to the early detection and exclusion system, to the European Court of Auditors, to the Financial Irregularities Panel, to the European Anti-Fraud Office or to the European Public Prosecutor’s Office.

[* Delete as applicable]

[If this declaration is being completed by a consortium member:

The following table contains our financial data as included in the consortium’s tender form. These data are based on our annual closed accounts and our latest projections. Estimated figures (i.e. those not included in annual closed accounts) are given in italics. Figures in all columns have been provided on the same basis to allow a direct, year-on-year comparison to be made <except as explained in the footnote to the table>.

| Financial data Data requested in this table must be consistent with the selection criteria set in the additional information about the contract notice document | 2 years before last5 <specify> EUR | Year before last year <specify> EUR | Last year <specify> EUR | Average6 EUR | Past year EUR] | [Current year EUR] |
| --- | --- | --- | --- | --- | --- | --- |
| Annual turnover 7, excluding this contract |  |  |  |  |  |  |
| Current assets8 |  |  |  |  |  |  |
| Current liabilities9 |  |  |  |  |  |  |
| [Current ratio (current assets/current liabilities) | Not applicable | Not applicable |  | Not applicable | Not applicable | Not applicable] |

The following table contains our personnel statistics as included in the consortium’s tender form:

| Annual manpower | Year before past year |  | Past year |  | Current year |  | Period average |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Overall | Relevant fields11 | Overall | Relevant fields11 | Overall | Relevant fields 11 | Overall | Relevant fields 11 |
| Permanent personnel 12 |  |  |  |  |  |  |  |  |
| Other personnel 13 |  |  |  |  |  |  |  |  |
| Total |  |  |  |  |  |  |  |  |
| Permanent personnel as a proportion of total personnel (%) | % | % | % | % | % | % | % | % |

Yours faithfully

Name and first name: <…………………………………………………………………>

Duly authorised to sign this tender on behalf of:

<……………………………………………………………………………………>

Place and date: <…………………………………………………………….………….>

Stamp of the firm/company:

This tender includes the following annexes:

<Numbered list of annexes with titles>

ANNEX 1
DECLARATION ON HONOUR ON EXCLUSION AND SELECTION CRITERIA

[How to submit the Declaration on Honour:

Insert here form A14a, available at the following link: http://ec.europa.eu/europeaid/prag/annexes.do?chapterTitleCode=A

For the Declaration on Honour, different steps are applicable depending on the type of procedure. The applicable procedure can be verified in your letter of invitation.

Open tender procedure

For supply tenders where the instructions to tenderers (see section 10) state that the tender should be submitted by post or courier or hand delivered (paper submission):

- each legal entity identified under point 1, including every consortium member, and capacity-providing entities (if any) signs and dates the declaration on honour

- when submitting the tender, copies of the declaration on honour are provided

- the leader of the consortium keeps the original declarations on honour, including the declarations on honour of every consortium member, and capacity-providing entities (if any)

- during the evaluation, the evaluation committee might request the submission of the original declarations on honour, including the declarations on honour of every consortium member, and capacity-providing entities (if any)

For supply tenders where the instructions to tenderers (see section 10) state that the tender should be submitted via eSubmission:

- each legal entity identified under point 1, including every consortium member, and capacity-providing entities (if any) sign and date the declaration on honour

- the declarations on honour are scanned and submitted via eSubmission through the section “Declaration on Honour” under “Attachments”.

- the leader of the consortium keeps the original declarations on honour, including the declarations on honour of every consortium member, and capacity-providing entities (if any)

- during the evaluation, the evaluation committee might request the submission of the original declarations on honour, including the declarations on honour of every consortium member, and capacity-providing entities (if any)

Negotiated procedure managed directly managed by the European Union

- each legal entity identified under point 1, including every consortium member, and capacity-providing entities (if any) signs and dates the Declaration on Honour

- the Declaration on Honour is scanned and submitted via eSubmission through the section “Declaration on Honour” under “Attachments”.

- In case the  Declaration on Honour is signed with a Qualified Electronic Signature (QES), submit the QES-signed Declaration on Honour via eSubmission through the section “Declaration on Honour” under “Attachments”.

- In case the  Declaration(s) on Honour is signed with a blue ink signature, send the hand-signed original by letter to the contracting authority's postal address specified under Section 8 of Instructions to Tenderers at the latest on the first working day following the electronic submission of tender. The envelope, clearly mentioning the reference to the call for tenders and the eSubmission ID of the tender must be marked as "CALL FOR TENDERS – NOT TO BE OPENED BY THE INTERNAL MAIL DEPARTMENT". Only the original of the Declaration on Honour should be sent by letter, no other documents.

Simplified procedure, local open procedure and negotiated procedure indirectly managed by an EU partner country

- each legal entity identified under point 1, including every consortium member, and capacity-providing entities (if any) signs and dates the declaration on honour

- when submitting the tender, the signed and dated declaration on honour shall be included

- In case the Qualified Electronic Signature (QES) is used for the signing of the Declaration(s) on honour, submit the QES-signed Declaration on Honour by email.

Delete this section highlighted in yellow after having completed all instructions.]

Declaration on honour on
exclusion criteria and selection criteria

The undersigned [insert name of the signatory of this form], representing:

| (only for natural persons) himself or herself | (only for legal persons) the following legal person: |
| --- | --- |
| ID or passport number: (‘the person’) | Full official name: Official legal form: Statutory registration number: Full official address: VAT registration number: (‘the person’) |

The person is not required to submit the declaration on exclusion criteria if the same declaration has already been submitted for the purposes of another award procedure of the same contracting authority, provided the situation has not changed, and that the time that has elapsed since the issuing date of the declaration does not exceed one year.

In this case, the signatory declares that the person has already provided the same declaration on exclusion criteria for a previous procedure and confirms that there has been no change in its situation:

| Date of the declaration | Full reference to previous procedure |
| --- | --- |

I – Situations of exclusion concerning the person

| - declares that the person is in one of the following situations: | YES | NO |
| --- | --- | --- |
| - it is bankrupt, subject to insolvency or winding-up procedures, its assets are being administered by a liquidator or by a court, it is in an arrangement with creditors, its business activities are suspended or it is in any analogous situation arising from a similar procedure provided for under Union or national law; |  |  |
| - it has been established by a final judgement or a final administrative decision that the person is in breach of its obligations relating to the payment of taxes or social security contributions in accordance with the applicable law; |  |  |
| - it has been established by a final judgement or a final administrative decision that the person is guilty of grave professional misconduct by having violated applicable laws or regulations or ethical standards of the profession to which the person belongs, or by having engaged in any wrongful conduct which has an impact on its professional credibity where such conduct denotes wrongful intent or gross negligence, including, in particular, any of the following: |  |  |
| (i) fraudulently or negligently misrepresenting information required for the verification of the absence of grounds for exclusion or the fulfilment of eligibility or selection criteria or in the performance of a contract or an agreement; |  |  |
| (ii) entering into agreement with other persons with the aim of distorting competition; |  |  |
| (iii) violating intellectual property rights; |  |  |
| (iv) attempting to influence the decision-making process of the contracting authority during the award procedure; |  |  |
| (v) attempting to obtain confidential information that may confer upon it undue advantages in the award procedure; |  |  |
| - it has been established by a final judgement that the person is guilty of any of the following: |  |  |
| (i) fraud, within the meaning of Article 3 of Directive (EU) 2017/1371 and Article 1 of the Convention on the protection of the European Communities' financial interests, drawn up by the Council Act of 26 July 1995; |  |  |
| (ii) corruption, as defined in Article 4(2) of Directive (EU) 2017/1371 or active corruption within the meaning of Article 3 of the Convention on the fight against corruption involving officials of the European Communities or officials of Member States of the European Union, drawn up by the Council Act of 26 May 1997, or conduct referred to in Article 2(1) of Council Framework Decision 2003/568/JHA, or corruption as defined in other applicable laws; |  |  |
| (iii) conduct related to a criminal organisation, as referred to in Article 2 of Council Framework Decision 2008/841/JHA; |  |  |
| (iv) money laundering or terrorist financing, within the meaning of Article 1(3), (4) and (5) of Directive (EU) 2015/849 of the European Parliament and of the Council; |  |  |
| (v) terrorist offences or offences related to terrorist activities as well as of inciting, aiding, abetting or attempting to commit such offences as defined in Articles 3, 14 and Title III of Directive (EU) 2017/541 of the European Parliament and of the Council of 15 March 2017 on combating terrorism; |  |  |
| (vi) child labour or other offences concerning trafficking in human beings as referred to in Article 2 of Directive 2011/36/EU of the European Parliament and of the Council; |  |  |
| - it has shown significant deficiencies in complying with the main obligations in the performance of a contract or an agreement financed by the Union’s budget, which has led to its early termination or to the application of liquidated damages or other contractual penalties, or which has been discovered following checks, audits or investigations by a contracting authority, the European Anti-Fraud Office (OLAF) or the Court of Auditors; |  |  |
| - it has been established by a final judgment or final administrative decision that the person has committed an irregularity within the meaning of Article 1(2) of Council Regulation (EC, Euratom) No 2988/95; |  |  |
| - it has been established by a final judgment or final administrative decision that the person has created an entity under a different jurisdiction with the intent to circumvent fiscal, social or any other legal obligations in the jurisdiction of its registered office, central administration or principal place of business. |  |  |
| - (only for legal persons) it has been established by a final judgment or final administrative decision that the person has been created with the intent provided for in point (g). |  |  |
| - declares that, for the situations referred to in points (1) (c) to (1) (h) above, in the absence of a final judgement or a final administrative decision, the person is: | YES | NO |
| - subject to facts established in the context of audits or investigations carried out by the European Public Prosecutor's Office, the Court of Auditors, or the internal auditor, or any other check, audit or control performed under the responsibility of an authorising officer of an EU institution, of a European office or of an EU agency or body; |  |  |
| - subject to non-final judgments or non-final administrative decisions which may include disciplinary measures taken by the competent supervisory body responsible for the verification of the application of standards of professional ethics; |  |  |
| - subject to facts referred to in decisions of entities or persons being entrusted with EU budget implementation tasks; |  |  |
| - subject to information transmitted by Member States implementing Union funds; |  |  |
| - subject to decisions of the Commission relating to the infringement of Union competition law or of a national competent authority relating to the infringement of Union or national competition law; |  |  |
| - informed, by any means, that it is subject to an investigation by the European Anti-Fraud office (OLAF): either because it has been given the opportunity to comment on facts concerning it by OLAF, or it has been subject to on-the-spot checks by OLAF in the course of an investigation, or it has been notified of the opening, the closure or of any circumstance related to an investigation of the OLAF concerning it. |  |  |

II – Situations of exclusion concerning natural or legal persons with power of representation, decision-making or control over the legal person and beneficial owners

Not applicable to natural persons, Member States and local authorities

| - declares that a natural or legal person who is a member of the administrative, management or supervisory body of the above-mentioned legal person, or who has powers of representation, decision or control with regard to the above-mentioned legal person (this covers e.g. company directors, members of management or supervisory bodies, and cases where one natural or legal person holds a majority of shares), or a beneficial owner of the person (as referred to in point 6 of article 3 of Directive (EU) No 2015/849) is in one of the following situations: | YES | NO | N/A |
| --- | --- | --- | --- |
| Situation (1)(c) above (grave professional misconduct) |  |  |  |
| Situation (1)(d) above (fraud, corruption or other criminal offence) |  |  |  |
| Situation (1)(e) above (significant deficiencies in performance of a contract ) |  |  |  |
| Situation (1)(f) above (irregularity) |  |  |  |
| Situation (1)(g) above (creation of an entity with the intent to circumvent legal obligations) |  |  |  |
| Situation (1)(h) above (person created with the intent to circumvent legal obligations) |  |  |  |

III – Situations of exclusion concerning natural or legal persons assuming unlimited liability for the debts of the legal person

| - declares that a natural or legal person that assumes unlimited liability for the debts of the above-mentioned legal person is in one of the following situations [If yes, please indicate in annex to this declaration which situation and the name(s) of the concerned person(s) with a brief explanation]: | YES | NO | N/A |
| --- | --- | --- | --- |
| Situation (a) above (bankruptcy) |  |  |  |
| Situation (b) above (breach in payment of taxes or social security contributions) |  |  |  |

IV – Other Grounds for rejection from this procedure

| - declares that the above-mentioned person: | YES | NO |
| --- | --- | --- |
| Was previously involved in the preparation of the procurement documents used in this award procedure, where this entailed a breach of the principle of equality of treatment including distortion of competition that cannot be remedied otherwise. |  |  |

V – Remedial measures

If the person declares one of the situations of exclusion listed above, it may indicate remedial measures it has taken to remedy the exclusion situation, in order to allow the authorising officer to determine whether such measures are sufficient to demonstrate its reliability. This may include e.g. technical, organisational and personnel measures to prevent further occurrence, compensation of damage or payment of fines or of any taxes or social security contributions. The relevant documentary evidence which illustrates the remedial measures taken must be provided in annex to this declaration. This does not apply for situations referred in point (1)(d) of this declaration.

VI – Evidence upon request

Upon request and within the time limit set by the contracting authority the person must provide information on natural or legal persons that are members of the administrative, management or supervisory body or that have powers of representation, decision or control, including legal and natural persons within the ownership and control structure and beneficial owners and appropriate evidence that none of those persons are in one of the exclusion situations referred to in (1) (c) to (f).

It must also provide the following evidence concerning the person itself and the natural or legal persons on whose capacity the person intends to rely, or a subcontractor and concerning the natural or legal persons which assume unlimited liability for the debts of the person:

For situations described in (1): (a), (c), (d), (f), (g) and (h) above, production of a recent extract from the judicial record is required or, failing that, an equivalent document recently issued by a judicial or administrative authority in the country of establishment of the person showing that those requirements are satisfied.

For the situation described in point (1) (a), (b), production of recent certificates issued by the competent authorities of the country of establishment. These documents must provide evidence covering all taxes and social security contributions for which the person is liable, including for example, VAT, income tax (natural persons only), company tax (legal persons only) and social security contributions. Where any document described above is not issued in the country concerned, it may be replaced by a sworn statement made before a judicial authority or notary or, failing that, a solemn statement made before an administrative authority or a qualified professional body in its country of establishment.

The person is not required to submit the evidence if it has already been submitted for another award procedure of the same contracting authority. The documents must have been issued no more than one year before the date of their request by the contracting authority and must still be valid at that date.

The signatory declares that the person has already provided the documentary evidence for a previous procedure and confirms that there has been no change in its situation:

| Document | Full reference to previous procedure |
| --- | --- |
| Insert as many lines as necessary. |  |

The person is not required to submit the evidence if it can be accessed on a national database free of charge.

The signatory declares that the following internet address of the database/identification data provide access to the evidence required.

| Internet address of the database | Identification data of the document |
| --- | --- |
| Insert as many lines as necessary. |  |

VII – Selection criteria

Selection criteria applicable to all consortium members/subcontractors/capacity providing entities

| - declares that the above-mentioned person complies with the selection criteria applicable to it individually as provided in the tender documents: | YES | NO | N/A |
| --- | --- | --- | --- |
| - It has the legal and regulatory capacity to pursue the professional activity needed for performing the contract as required in section [insert] of the contract notice/Instructions to tenderers; |  |  |  |
| - It fulfills the applicable economic and financial criteria indicated in section [insert] of the contract notice/additional information about the contract notice/Instructions to tenderers; |  |  |  |
| - It fulfills the applicable technical criteria indicated in section [insert] of the contract notice/additional information about the contract notice /Instructions to tenderers. |  |  |  |
| - It fulfills the applicable professional criteria indicated in section [insert] of the contract notice/additional information about the contract notice/Instructions to tenderers. |  |  |  |
| - is not subject to conflicting interests which may negatively affect the contract performance. |  |  |  |

Please adapt the table above to the criteria indicated in the tender documents (i.e. insert extra rows for each criterion or delete irrelevant rows).

Selection criteria applicable to the tenderer as a whole-consolidated assessment

(to be filled ONLY by the sole tenderer or the leader in case of consortium)

| - if the above-mentioned person is the sole tenderer or the leader in case of consortium, declares that: | YES | NO | N/A |  |
| --- | --- | --- | --- | --- |
| - the tenderer, including all members of the group in case of consortium and including subcontractors and entities on whose capacity the tenderer intends to rely if applicable, fulfils all the selection criteria for which a consolidated assessment will be made as provided in the tender documents. |  |  |  |  |
| - is not subject to conflicting interests which may negatively affect the contract performance. |  |  |  |  |

In case of a procedure with lots the above statements apply to the lot(s) for which the request to participate/tender is submitted.

VIII – Evidence for selection

The signatory declares that the above-mentioned person is able to provide the necessary supporting documents listed in the relevant sections of the tender documents and which are not available electronically upon request and without delay.

Where the evidence is not required to be provided with the request to participate/tender, the person is invited to prepare in advance the documents related to the evidence, since the contracting authority may request to provide these in a short deadline.

The person is not required to submit the evidence if it has already been submitted for another procurement procedure of the same contracting authority. The documents must have been issued no more than one year before the date of their request by the contracting authority and must still be valid at that date.

The signatory declares that the person has already provided the documentary evidence for a previous procedure and confirms that there has been no change in its situation:

| Document | Full reference to previous procedure |
| --- | --- |
| Insert as many lines as necessary. |  |

The person is not required to submit the evidence if it can be accessed on a national database free of charge.

The signatory declares that the following internet address of the database/identification data provide access to the evidence required.

| Internet address of the database | Identification data of the document |
| --- | --- |
| Insert as many lines as necessary. |  |

IX - Declaration on honour on established debt to the union

(to be filled ONLY by the sole tenderer or the leader in case of consortium)

The person, being a sole tenderer/the leader in case of consortium, submitting a request to participate/tender for the above procedure, declares that:

| the tenderer, including each member of the group in case of consortium, subcontractors, | YES | NO |
| --- | --- | --- |
| does not have an established debt to the Union. |  |  |

The above-mentioned person must immediately inform the contracting authority of any changes in the situations as declared.

The above-mentioned person may be subject to rejection from this procedure and to administrative sanctions (exclusion or financial penalty) if any of the declarations or information provided as a condition for participating in this procedure prove to be false.

Full name	Date	Signature

PROVISIONAL / FINAL ACCEPTANCE CERTIFICATE

Contract No:     PILOT 04 /SAVE WATER / Lot 1

Title: Water Supply Products for the Water Supply System (supply and installation) / LOT 1 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

Contractor: …………………………	Beneficiary: ………………………………

……………………..	……………………

……………………..	…………………….

| Item | qty | Description | Delivery | [Installation] | [Spare Parts] | [Consumables] | [(Manuals] | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 2 3 4 | <…> <…> <…> <…> | <……………………> <……………………> <……………………> <……………………> |  |  |  |  |  |  |

Provisional:	All of the above-mentioned items have been delivered, installed, tested and found compliant with the technical specifications of the supply contract. The contractor has also demonstrated that the obligations in the Communication and Visibility Manual have been complied with (Article 7.8 in the general conditions).

Final:	The contractor has remedied any defect or damage occurred during the warranty period, as specified in the contract.

(delete not applicable)

Date of acceptance……………….

The contractor	The Supervisor

Name	Name

Signature…………………………..	Signature…………………………..

The project manager (contracting authority)

Name

Signature…………………………..

PROVISIONAL / FINAL ACCEPTANCE CERTIFICATE

Contract No:     PILOT 04 /SAVE WATER / Lot 2

Title: Sensors for the monitoring of Water Supply System (supply and installation) / LOT 2 for improving the supply of drinking water in the municipality of Vlora in the frame of the implementation of the project SAVE WATER: « Improving water management and supply infrastructure via smart technologies, policies and tools.

Contractor: …………………………	Beneficiary: ………………………………

……………………..	……………………

……………………..	…………………….

| Item | qty | Description | Delivery | [Installation] | [Spare Parts] | [Consumables] | [(Manuals] | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 2 3 4 | <…> <…> <…> <…> | <……………………> <……………………> <……………………> <……………………> |  |  |  |  |  |  |

Provisional:	All of the above mentioned items have been delivered, installed, tested and found compliant with the technical specifications of the supply contract. The contractor has also demonstrated that the obligations in the Communication and Visibility Manual have been complied with (Article 7.8 in the general conditions).

Final:	The contractor has remedied any defect or damage occurred during the warranty period, as specified in the contract.

(delete not applicable)

Date of acceptance:………………….

The contractor	The Supervisor

Name	Name

Signature…………………………..	Signature…………………………..

The project manager (contracting authority)

Name

Signature…………………………..

External action financial instruments and 
European Development Fund

Rules on participation in procurement procedures and grants

TABLE OF CONTENT

Part I: 2014-2020 instruments for external action	2

1) DCI, ENI, PI, Greenland and INSC	2

2) IcSP and EIDHR	3

3) IPA II	3

Part II: Rules on nationality and origin for public procurement, grants and other award procedures financed under the ACP-EC Partnership Agreement, laid down in Annex IV to the latter Agreement as revised by Decision No 1/2014 of the ACP-EU Council of Ministers of 20 June 2014 (2014/428/EU)	4

Part III: rules on nationality and origin for public procurement, grants and other award procedures for instruments for external action financed under the Overseas Association Decision	5

Appendices	6

- Part I: 2014-2020 instruments for external action

- 1)	Eligible countries for DCI, ENI , PI, Greenland and INSC (CIR - Article 9)

- Participation in the award of procurement contracts, grants and other award procedures for actions financed under DCI, ENI, PI, Greenland and INSC for the benefit of third parties shall be open to all natural persons who are nationals of, and legal persons that are effectively established in, one of the following eligible countries/territories/beneficiaries:

- EU Member States (appendix 1)

- IPA II beneficiaries (listed in the Annex I of IPA II Instrument (appendix 2)

- European Economic Area (appendix 3)

- Developing countries and territories, (included in the OECD-DAC list of ODA recipients), which are not members of the G20 group:

- Least Developed Countries (LDCs) (appendix 4)

- Other Low Income Countries (appendix 5)

- Lower Middle Income Countries and Territories (appendix 6)

- Upper Middle Income Countries and Territories (appendix 7)

- Overseas Countries and Territories (OCTs) covered by Council Decision 2013/755/EU of 25 November 2013 on the association of the overseas countries and territories with the European Union (appendix 8)

- Member States of the OECD (appendix 9) are also eligible when contracts are exclusively implemented in a Least Developed Country or in a Highly Indebted Poor Country (HIPC).

- (i)	Developing countries, as included in the list of ODA recipients, which are members of the G20 group (appendix 10);

- (ii)	any other countries and territories (ie. all countries of the world).

- The entities of these countries can only participate in procedures, where the country itself is a beneficary of the action. This can happen in particular, in thematic programmes, programmes financed under the PI or where the success of a regional programme necessitates the participation of the said country.

- any countries for which reciprocal access to external assistance is established by the Commission.

- Currently there are no such countries.

- for ENI Instrument only: in addition to the countries/territories/beneficiaries mentioned above that are eligible for ENI, the following countries/territories are also considered eligible for contracts financed under the ENI Instrument:

- (i)	Partner countries or territories covered by the Instrument (annex I of the ENI Intrument) (appendix 11);

- (ii)	in the case of relevant procedures taking place in the context of the multi-country and cross-border co-operation programmes in which it participates: the Russian Federation.

- For DCI, ENI, PI, Greenland and INSC: where an agreement on widening the market for procurement of goods or services to which the Union is party applies, the procurement procedures for contracts financed by the budget shall also be open to natural and legal persons established in a third country other than those specified in the basic instruments governing the cooperation sector concerned, under the conditions laid down in that agreement.

- 2)	for IcSP and EIDHR (CIR – Article 11)

- All countries are eligible for participation in contracts financed under these Intruments that are fully untied without prejudice to the limitations inherent to the nature and the objectives of the action.

- 3)	for IPA II (CIR- Article 10)

- Participation in the award of procurement contracts, grants and other award procedures for actions financed under the CIR for IPA II for the benefit of third parties shall be open to all natural persons who are nationals of, and legal persons who are effectively established in, one of the following eligible countries/ territories/beneficiaries:

  - EU Member States (appendix 1)

  - Beneficiaries listed in the Annex I of the IPA II (appendix 2)

  - European Economic Area (appendix 3)

  - Partner countries and territories covered by ENI Instrument (annex I of ENI Intrument) (appendix 11)

  - countries for which Commission has adopted a decision approving the request for reciprocal access to external assistance.

- Currently there are no such countries.

  - where an agreement on widening the market for procurement of goods or services to which the Union is party applies, the procurement procedures for contracts financed by the budget shall also be open to natural and legal persons established in a third country other than those specified in the basic instruments governing the cooperation sector concerned, under the conditions laid down in that agreement.

- Part II: Rules on nationality and origin for public procurement, grants and other award procedures financed under the ACP-EC Partnership Agreement, laid down in Annex IV to the latter Agreement as revised by Decision No 1/2014 of the ACP-EU Council of Ministers of 20 June 2014 (2014/428/EU)

Participation in procedures for the award of procurement contracts or grants financed from the multi-annual financial framework of cooperation under the ACP-EC Partnership Agreement is open to all natural persons who are nationals of, or legal persons who are effectively established in:

  - an ACP State (appendix 12);

  - a Member State of the European Union (appendix 1);

  - Beneficiaries of the Instrument for pre-accession assistance (appendix 2);

  - a Member State of the European Economic Area (appendix 3);

  - Overseas Countries and Territories (appendix 8);

  - developing countries and territories, as included in the OECD-DAC list of ODA Recipients, which are not members of the G20 group, without prejudice to the status of the Republic of South Africa, as governed by Protocol 3 of the partnership Agreement (appendices 4, 5, 6 and 7);

  - countries for which Commission has adopted a decision approving the request for reciprocal access to external assistance in agreement with ACP countries;

Currently there are no such countries.

  - a Member State of the OECD (appendix 9), in the case of contracts exclusively implemented in a Least Developed Country (LDC) or a Highly Indebted Poor Country (HIPC).

- Part III: rules on nationality and origin for public procurement, grants and other award procedures for instruments for external action financed under the Overseas Association Decision.

From the publication of the COUNCIL DECISION 2013/755/EU of 25 November 2013 on the association of the overseas countries and territories with the European Union (‘Overseas Association Decision’) the following rules are applicable to calls financed under the financial assistance of the EDF:

- Tenderers, applicants and candidates from the following countries and territories shall be eligible to funding under this Decision:

- Member States of the European Union (appendix 1)

- candidate countries and potential candidates as recognised by the Union (appendix 2)

- members of the European Economic Area (appendix 3)

- OCTs (appendix 8)

- developing countries and territories, as included in the OECD-DAC list of ODA Recipients, which are not members of the G-20 group (appendices 4, 5, 6 and 7)

- countries for which reciprocal access to external assistance is established by the Commission. Reciprocal access may be granted, for a limited period of at least one year, whenever a country grants eligibility on equal terms to entities from the Union and from OCTs;

Currently there are no such countries.

- Member States of the OECD (appendix 9), in the case of contracts exclusively implemented in a Least Developed Country.

- APPENDICES

APPENDIX 1 : EU MEMBER STATES

- Austria, Belgium, Bulgaria, Czech Republic, Croatia, Cyprus, Denmark, Estonia, Finland, France, Germany, Greece, Hungary, Ireland, Italy, Latvia, Lithuania, Luxembourg, Malta, Netherlands, Poland, Portugal, Romania, Slovakia, Slovenia, Spain, Sweden, United Kingdom.

APPENDIX 2 : IPA II beneficiaries

- Albania, Bosnia and Herzegovina, Kosovo*, Montenegro, Serbia, Turkey, Republic of North Macedonia.

- * This designation is without prejudice to positions on status, and is in line with UNSCR 1244/1999 and the ICJ Opinion on the Kosovo declaration of independence.

- APPENDIX 3 : European Economic Area

- (only non-EU MS are mentioned) Iceland, Lichtenstein, Norway.

- APPENDIX 4 : Least Developed Countries

Afghanistan, Angola, Bangladesh, Benin, Bhutan, Burkina Faso, Burundi, Cambodia, Central African Republic, Chad, Comoros, Democratic Republic of the Congo, Djibouti, Eritrea, Ethiopia, Gambia, Guinea, Guinea-Bissau, Haiti, Kiribati, Lao People's Democratic Republic, Lesotho, Liberia, Madagascar, Malawi, Mali, Mauritania, Mozambique, Myanmar, Nepal, Niger, Rwanda, Sao Tome & Principe, Senegal, Sierra Leone, Solomon Islands, Somalia, Sudan, South Sudan, Tanzania, Timor-Leste, Togo, Tuvalu, Uganda, Yemen, Zambia.

- APPENDIX 5: Other Low Income Countries

Democratic People’s Republic of Korea, Zimbabwe.

APPENDIX 6 : Lower Middle Income Countries and Territories

Armenia, Bolivia, Cabo Verde, Cameroon,  Congo, Côte d´Ivoire, Egypt, El Salvador, Eswatini, Georgia, Ghana, Guatemala, Honduras, India, Indonesia, Jordan, Kenya, Kosovo, Kyrgyzstan, Micronesia, Moldova, Mongolia, Morocco, Nicaragua, Nigeria, Pakistan, Papua New Guinea, Philippines, Sri Lanka, Syrian Arab Republic, Tajikistan, Tokelau, Tunisia, Ukraine, Uzbekistan, Vanuatu, Vietnam, West Bank and Gaza Strip.

APPENDIX 7 : Upper Middle Income Countries and Territories

Albania, Algeria, Antigua and Barbuda, Argentina, Azerbaijan, Belarus, Belize, Bosnia and Herzegovina, Botswana, Brazil, China (People’s Republic of), Colombia, Costa Rica, Cuba, Dominica, Dominican Republic, Ecuador, Equatorial Guinea, Fiji, Republic of North Macedonia, Gabon, Grenada, Guyana, Iran, Iraq, Jamaica, Kazakhstan, Lebanon, Libya, Malaysia, Maldives, Marshall Islands,  Mauritius, Mexico, Montenegro, Montserrat, Namibia, Nauru, Niue, Palau, Panama, Paraguay, Peru, Saint Helena, Saint Lucia, Saint Vincent & the Grenadines, Samoa, Serbia, South-Africa, Suriname, Thailand, Tonga,  Turkey, Turkmenistan, Venezuela, Wallis and Futuna.

APPENDIX 8 : overseas countries and territories

- Anguilla (UK), Aruba (NL), Bermuda (UK), Bonaire (NL), British Antarctic Territory (UK), British Indian Ocean Territory (UK), British Virgin Islands (UK), Cayman Islands (UK), Curação (NL), Falkland Islands (UK), French Polynesia (FR), French Southern and Antarctic Territories (FR), Greenland (DK), Montserrat (UK), New Caledonia and Dependencies (FR), Pitcairn (UK), Saba (NL), Saint Barthelemy (FR), Saint Helena, Ascension and Tristan da Cunha (UK), Sint Eustatius (NL), Sint Maarten (NL), South Georgia and South Sandwich Islands (UK), St. Pierre and Miquelon (FR), Turks and Caicos (UK), Wallis and Futuna Islands (FR).

APPENDIX 9 : OECD MEMBER STATES

- Austria, Belgium, Czech Republic, Denmark, Estonia, Finland, France, Germany, Greece, Hungary, Ireland, Italy, Latvia, Lithuania, Luxembourg, Netherlands, Poland, Portugal, Slovakia, Slovenia, Spain, Sweden, United Kingdom.

- Australia, Canada, Chile, Iceland, Israel, Japan, Korea, Mexico, New Zealand, Norway, Switzerland, Turkey, United States of America.

APPENDIX 10 : G20 member developing countries

- Argentina, Brazil, China, India, Indonesia, Mexico, South-Africa, Turkey.

APPENDIX 11 : ENI PARTNER COUNTRIES AND TERRITORIES

- Algeria, Armenia, Azerbaijan, Belarus, Egypt, Georgia, Israel, Jordan, Lebanon, Libya, Republic of Moldova, Morocco, occupied Palestinian territory (oPt), Syria, Tunisia, Ukraine.

APPENDIX 12 : ACP COUNTRIES*

Africa:

South Africa**, Angola, Benin, Botswana, Burkina Faso, Burundi, Central African Republic, Cameroon, Cabo Verde, Chad, Comoros Islands, Congo, Côte d'Ivoire, Democratic Republic of the Congo, Djibouti, Eritrea, Eswatini, Ethiopia, Gabon, Gambia, Ghana, Guinea, Guinea-Bissau, Equatorial Guinea, Kenya, Lesotho, Liberia, Madagascar, Malawi, Mali, Mauritius, Mauritania, Mozambique, Namibia, Niger, Nigeria, Uganda, Rwanda, Sao Tome and Principe, Senegal, Seychelles, Sierra Leone, Somalia, Sudan, , Tanzania, Togo, Zambia and Zimbabwe.

Caribbean:

Antigua and Barbuda, Bahamas, Barbados, Belize, Dominica, Dominican Republic, Grenada, Guyana, Haiti, Jamaica, Saint Kitts and Nevis, Saint Lucia, Saint Vincent and the Grenadines, Surinam, Trinidad and Tobago.

Pacific:

Cook Islands, East Timor, Fiji, Kiribati, Marshall Islands, Micronesia, Nauru, Niue, Palau, Papua New Guinea, the Solomon Islands, Western Samoa, Tonga, Tuvalu, Vanuatu.

**	While natural and legal persons established in South Africa are eligible to participate in procedures financed by the 10th/ 11th EDF, South Africa cannot be a beneficiary of contracts financed by the 10th/11th EDF.

*	Cotonou Partnership Agreement of 23 June 2000 (as amended by the provisional application of Decision No 1/2000 of the ACP-EC Council of Ministers of 27 July 2000, Decision No 1/2000 of the ACP-EC customs cooperation committee of 18 October 2000, Decision No 1/2001 of the ACP-EC customs cooperation committee of 20 April 2001, Decision No 2/2001 of the ACP-EC customs cooperation committee of 20 April 2001, Decision No 3/2001 of the ACP-EC customs cooperation committee of 10 May 2001, Decision No 4/2001 of the ACP-EC customs cooperation committee of 27 June 2001, Decision No 5/2001 of the ACP-EC customs cooperation committee of 7 December 2001, Decision No 2/2002 of the ACP-EC customs cooperation committee of 28 October 2002, Decision No 1/2003 of the ACP-EC Council of Ministers of 16 may 2003, Council Decision (EC) of 19 December 2002, Decision No 1/2004 of the ACP-EC Council of Ministers of 6 may 2004, Decision No 2/2004 of the ACP-EC customs cooperation committee of 30 June 2004 and Decision No 4/2005 of the ACP-EC customs cooperation committee of 13 April 2005).

- FINANCIAL IDENTIFICATION – PDF ATTACHED

- LEGAL ENTITY – NATURAL PERSON– PDF ATTACHED

- LEGAL ENTITY - PRIVATE/PUBLIC LAW BODY WITH LEGAL FORM– PDF ATTACHED

- LEGAL ENTITY – PUBLIC LAW BODY– PDF ATTACHED

- ANNEX I: GENERAL CONDITIONS– PDF ATTACHED

- Foto te pompave  – PDF ATTACHED

The Common Procurement Vocabulary (CPV) is the mandatory reference nomenclature applicable to procurement contracts. The list of CPV codes is available on:  http://simap.ted.europa.eu/en/web/simap/cpv

Regulation (EU) 2021/1529 of the European Parliament and of the Council of 15 September 2021 establishing the Instrument for Pre-Accession assistance (IPA III); OJ L 330, 20.9.2021, p. 1–26.

It is recommended to use registered mail in case the postmark would not be readable.

https://ec.europa.eu/info/funding-tenders/opportunities/portal/screen/home

DDP (Delivered Duty Paid) — Incoterms 2020 International Chamber of Commerce http://www.iccwbo.org/incoterms/

See PRAG Section 2.6.10.1.3 A)

It is recommended to use registered mail in case the postmark would not be readable

DDP (Delivered Duty Paid) — Incoterms 2020 International Chamber of Commerce  http://www.iccwbo.org/incoterms/

Where the contracting party is an individual.

Where applicable. For individuals, mention their ID card or passport or equivalent document – number.

Except where the contracting party is not VAT registered.

DDP (Delivered Duty Paid) — Incoterms 2020 International Chamber of Commerce  http://www.iccwbo.org/incoterms/

See http://www.iccwbo.org/incoterms/

OJ L 205 of 21.11.2018, p. 39

Where the contracting party is an individual.

Where applicable. For individuals, mention their ID card or passport or equivalent document – number.

Except where the contracting party is not VAT registered.

DDP (Delivered Duty Paid) — Incoterms 2020 International Chamber of Commerce  http://www.iccwbo.org/incoterms/

See http://www.iccwbo.org/incoterms/

OJ L 205 of 21.11.2018, p. 39

[DDP (Delivered Duty Place)]  — Incoterms 2020 International Chamber of Commerce http://www.iccwbo.org/incoterms/

If the tender has been submitted by a consortium, the nationalities of all the consortium members must be eligible.

Applicable only to contracts financed by a basic act under the MFF 2014-2020 (contracts/lots above EUR 100 000 under CIR and independently of the value for other instruments).

The selection criteria, in the previous section of this form, have to be met before the technical requirements are assessed.

Country in which the legal entity is registered.

Add/delete additional lines for members as appropriate. Note that a capacity providing entity/ subcontractor is not considered to be a member for the purposes of this tender procedure. Subsequently, the data on capacity providing entities/ subcontractor must not appear in the data related to the economic, financial and professional capacity but on a separate document. If this tender is being submitted by an individual tenderer, the name of the tenderer should be entered as ‘leader’ (and all other lines should be deleted).

Natural persons have to prove their capacity in accordance with the selection criteria and by the appropriate means.

If this tender form is submitted by a consortium, the data in the table above must be the sum of the data in the corresponding tables in the declarations provided by the consortium members — see point 7 of this tender form. Consolidated data are not requested for financial ratios.

Last year=last accounting year for which the entity's accounts have been closed.

Amounts entered in the ‘Average’ column must be the mathematical average of the amounts entered in the three preceding columns of the same row.

The gross inflow of economic benefits (cash, receivables, other assets) arising from the ordinary operating activities of the enterprise (such as sales of goods, sales of services, interest, royalties, and dividends) during the year.

A balance sheet account that represents the value of all assets that are reasonably expected to be converted into cash within one year in the normal course of business. Current assets include cash, accounts receivable, inventory, marketable securities, prepaid expenses and other liquid assets that can be readily converted to cash.

A company's debts or obligations that are due within one year. Current liabilities appear on the company's balance sheet and include short term debt, accounts payable, accrued liabilities and other debts.

If this tender is submitted by a consortium, the data in the table above must be the sum of the data in the corresponding tables in the declarations provided by the consortium members — see point 7 of this tender form. Consolidated data are not requested for financial ratios.

Corresponding to the relevant specialisms identified in point 5 below.

Personnel directly employed or contracted by the tenderer on a permanent basis (i.e. under indefinite contracts).

Other personnel  directly employed or contracted by the tenderer on a non-permanent basis (i.e. under fixed-term contracts).

add/delete additional lines and/or rows as appropriate. If this tender is being submitted by an individual legal entity, the name of the legal entity should be entered as ‘Leader’ (and all other columns should be deleted).

References must be contracts implemented by the legal entity (or legal entities) submitting the-tender form (with the exception of documented cases of company buyout or universal succession). In the case of framework contracts (without contractual value), only specific contracts corresponding to assignments implemented under such framework contracts will be considered.

Amounts actually paid, without the effect of inflation.

The declaration under this point (2) is voluntary and it cannot have adverse legal effect on the economic operator until the conditions of Article 141(1) (a) FR are met.

The declaration is to be signed with:

- Electronic signature (recommended option):

In case you have the possibility to sign the declaration using a qualified electronic signature (QES), please have it signed electronically by your authorised representative(s). Please note that only the qualified electronic signature (QES) within the meaning of Regulation (EU) No 910/2014 (eIDAS Regulation) will be accepted.

Before sending back your electronically signed document, please check the signature and validity of the certificate with one of the following tools:

- DSS Demonstration validation tool available at https://ec.europa.eu/cefdigital/DSS/webapp-demo/validation can help you check the validity of a certificate by indicating the number and type of valid signatures in a document.

- EU Trusted List Browser can be consulted in order to check whether the electronic signature provider and the trust service it provides are part of European Union Trusted List: https://webgate.ec.europa.eu/tl-browser/#

To make sure you use a QES compliant to eIDAS Regulation, you need to check that both the service provider and the qualified certificate generation service used are included in the EU Trusted List Browser.

- Handwritten signature:

In case you do not have the possibility to sign the declaration using a qualified electronic signature (QES), please fill it in electronically, then print it and have it signed and dated by your authorised representative(s) using a hand-written signature.

Please check the DAC List of ODA Recipients, effective for reporting on 2018, 2019 and 2020 flows.

Non eligible G20 Members developing countries are: India, Indonesia, Argentina, Brazil, China, Mexico, South Africa. South Africa will be eligible when the action will be co-financed with the EDF. Turkey is also a developing country (upper middle income) G20 Member but is eligible as a beneficiary listed in the Annex I of the IPA II.

See appendix 4 for the full list of LDCs.

HIPCs are: Afghanistan, Benin, Bolivia, Burkina Faso, Burundi, Cameroon, Central African Republic, Chad, Comoros, Côte d’Ivoire, Democratic Republic of Congo, Ethiopia, Ghana, Guinea, Guinea-Bissau, Guyana, Haiti, Honduras, Liberia, Madagascar, Malawi, Mali, Mauritania, Mozambique, Nicaragua, Niger, Republic of Congo, Rwanda, São Tomé & Príncipe, Senegal, Sierra Leone, Tanzania, The Gambia, Togo, Uganda, Zambia.

In line with the upcoming corrigendum of the CIR, regarding Article 9(1)(b) (OJ L 316, 4.11.2014, p. 69) (FR).

See appendix 4 for the full list of LDCs.

See full list of HIPCs in footnote 4.

See appendix 4 for the full list of LDCs.

The United Kingdom ceased to be an EU Member State on the 31 of January 2020. Pursuant to the Withdrawal Agreement concluded between the EU and the UK, references to the eligibility of ‘Member States’ for participation in programmes under the current 2014-2020 MFF and the EDFs also cover the United Kingdom (Article 127(6), Article 137 and Article 152(1) Withdrawal Agreement).

As from 1 January 2021.

OCTs listed in Annex II to the TFEU having special relations with the United Kingdom are covered by the scope of the EU-UK Withdrawal Agreement. Therefore, pursuant to the EU-UK Withdrawal Agreement, Union law as referred to in Articles 137 WA therefore includes the rules on financing of OCTs and eligibility under the current 2014-2020 MFF and the EDFs (Article 3(1)(e), Article 127(6), Article 137 and Article 152(1),(3) Withdrawal Agreement).